## 23 05 13 - Meters and Gages for HVAC Piping

Requirements:  Refer to CSU Building Metering Guide.  Website:  http://www.calstate.edu/cpdc/ae/gsf/documents/CSU_Metering_Guide.pdf

Intent:  Metering to meet the performance-based LEED NC/EB Energy & Atmosphere Credit – Building-level energy metering standards for ongoing accountability and optimization of building energy and water consumption performance over time.

Refer to and coordinate with Section 25 00 00 – Integrated Automation.

Metering Equipment:  Allow Campus the ability to identify problems and achieve improved system performance.  Select meters for future connection to a remote-read automated metering network.

BTU meter shall be installed at each building and for each system (DHW and HHW).  Controlotron, EMCO ST30 Ultrasonic, or approved equal.

Flow Meters:

- Function:  Non-invasive flow measurement with a transmitter with 2-line backlit display with 4-button keypad.  Connect to Campus Energy Management System (EMS) by Siemens.

- Execution:  Locate on straight run of pipe with no flow interruptions such as valves or direction change.  Installed location shall typically have straight uninterrupted pipe for 10 diameters upstream and 5 diameters downstream.  Consult manufacturer’s installation instructions for specific installation requirements and other piping configurations.

- Website:  http://www.emcoflow.com/em_prods/sono_trak.aspx

### Keys for Cabinets and Padlocks:

- Cabinets and Equipment:  Provide 2 keys per panel.  Coordinate with Section 08 06 05 – Key Schedule.

- Padlocks:  Coordinate with Section 08 06 05 – Key Schedule.

- Closeout Submittal: Provide panel keys separated and labeled.  Provide location, room number, quantity, manufacturer name and model numbers of keys, and coordinate closeout submittal with Section 08 06 05 – Key Schedule.