## 23 20 00 - HVAC Piping and Pumps

Pumps: B&G, PACO, Armstrong, or approved equal, base-mounted or vertical pumps; no TACO, per Campus Standard.

Pump VFD: ABB model ACH550, or approved equal, with integral disconnect without bypass.

Above ground pipes: copper pipe, ProPress allowed for 2” or smaller.

Underground pipes: welded steel, pre-insulated with jacket. Maximum heating water supply temperature drop: 2°F drop from design based on 40°F ground temperature.