## 23 25 00 - HVAC Water Treatment

### Hydronic System:

Water Treatment for Hydronic System:  Coordinate with Project Manager to obtain current vendor’s product specifications for Contractor requirements on treatment for Hydronic System.

Campus Standard:  Water Treatment is provided by a vendor.  Specifications shall include requirement for Contractor to treat the Hydronic System in accordance with the vendor’s product specifications within a limited number of days after the system is charged.  The specifications shall include flushing, passivation, treatment with a cleaner and scale inhibitor, and circulation through a temporary 20 micron, maximum filter set.

Summary:  Related Sections:  Section 23 05 53.13 – Identification for Plumbing and HVAC Equipment.