- Section 23 05 19 - Meters and Gauges for HVAC Piping

PART 1 - GENERAL

REFERENCE STANDARDS

ASME B40.100 - Pressure Gauges and Gauge Attachments 2013.

ASME MFC-3M - Measurement of Fluid Flow in Pipes Using Orifice, Nozzle and Venturi 2004 (Reaffirmed 2017).

ASTM E1 - Standard Specification for ASTM Liquid-in-Glass Thermometers 2014.

ASTM E77 - Standard Test Method for Inspection and Verification of Thermometers 2014, with Editorial Revision (2017).

AWWA C700 - Cold-Water Meters -- Displacement Type, Metal Alloy Main Case 2015.

AWWA M6 - Water Meters -- Selection, Installation, Testing, and Maintenance 2012, with Addendum (2018).

UL 393 - Indicating Pressure Gauges for Fire-Protection Service Current Edition, Including All Revisions.

SUBMITTALS

Product Data: Provide list that indicates use, operating range, total range and location for manufactured components.

general information and design guidelines

Requirements:  Refer to CSU Building Metering Guide.  Website:  http://www.calstate.edu/cpdc/ae/gsf/documents/CSU_Metering_Guide.pdf

Intent:  Metering to meet the performance-based LEED NC/EB Energy & Atmosphere Credit – Building-level energy metering standards for ongoing accountability and optimization of building energy and water consumption performance over time.

Refer to and coordinate with Section 25 00 00 – Integrated Automation.

Metering Equipment:  Allow Campus the ability to identify problems and achieve improved system performance.  Select meters for future connection to a remote-read automated metering network.

BTU meter shall be installed at each building and for each system (DHW and HHW).  Controlotron, EMCO ST30 Ultrasonic, or approved equal.

Flow Meters:

Function:  Non-invasive flow measurement with a transmitter with 2-line backlit display with 4-button keypad.  Connect to Campus Energy Management System (EMS) by Siemens.

Execution:  Locate on straight run of pipe with no flow interruptions such as valves or direction change.  Installed location shall typically have straight uninterrupted pipe for 10 diameters upstream and 5 diameters downstream.  Consult manufacturer’s installation instructions for specific installation requirements and other piping configurations.

Website:  http://www.emcoflow.com/em_prods/sono_trak.aspx

Keys for Cabinets and Padlocks:

        - Cabinets and Equipment:  Provide 2 keys per panel.  Coordinate with Section 08 06 05 – Key Schedule.

        - Padlocks:  Coordinate with Section 08 06 05 – Key Schedule.

        - Closeout Submittal: Provide panel keys separated and labeled.  Provide location, room number, quantity, manufacturer name and model numbers of keys, and coordinate closeout submittal with Section 08 06 05 – Key Schedule.

PART 2 - PRODUCTS

POSITIVE DISPLACEMENT METERS (LIQUID)

AWWA C700, positive displacement disc type suitable for fluid with metal alloy main case and cast-iron frost-proof, breakaway bottom cap, hermetically sealed register, remote reading.

Meter: Brass body turbine meter with magnetic drive register.

Service: Cold water, 122 degrees F (50 degrees C).

Service: Hot water, 200 degrees F (93 degrees C).

Accuracy: 1-1/2 percent.

HEAT CONSUMPTION METERS

Meter: Brass body turbine meter with magnetic drive register, platinum temperature sensors.

Maximum Service Temperature: 200 degrees F (93 degrees C).

Accuracy: 1-1/2 percent.

LIQUID FLOW METERS

Calibrated ASME MFC-3M Venturi orifice plate and flanges with valved taps, chart for conversion of differential pressure readings to flow rate, with pressure gauge in case.

Annular element flow stations with meter set.

Measuring Station: Type 316 stainless steel pitot type flow element inserted through welded threaded couplet, with safety shut-off valves and quick coupling connections, and permanent metal tag indicating design flow rate, reading for design flow rate, metered fluid, line size, station or location number.

          - Pressure rating: 275 psi (1896 kPa).

          - Maximum temperature: 400 degrees F (204 degrees C).

          - Accuracy: Plus 0.55 percent to minus 2.30 percent.

PRESSURE GAUGES

Pressure Gauges: ASME B40.100, UL 393 drawn steel case, phosphor bronze bourdon tube, rotary brass movement, brass socket, with front recalibration adjustment, black scale on white background.

Mid-Scale Accuracy: One percent.

Scale: Psi and KPa.

PRESSURE GAUGE TAPPINGS

Gauge Cock: Tee or lever handle, brass for maximum 150 psi (1034 kPa).

Needle Valve: Brass, 1/4 inch (6 mm) NPT for minimum 150 psi (1034 kPa).

Pulsation Damper: Pressure snubber, brass with 1/4 inch (6 mm) connections.

Syphon: Steel, Schedule 40, 1/4 inch (6 mm) angle or straight pattern.

STEM TYPE THERMOMETERS

Thermometers - Fixed Mounting: Red- or blue-appearing non-toxic liquid in glass; ASTM E1; lens front tube, cast aluminum case with enamel finish.

Accuracy: 2 percent, per ASTM E77.

Calibration: Degrees F.

Thermometers - Adjustable Angle: Red- or blue-appearing non-toxic liquid in glass; ASTM E1; lens front tube, cast aluminum case with enamel finish, cast aluminum adjustable joint with positive locking device; adjustable 360 degrees in horizontal plane, 180 degrees in vertical plane.

Accuracy: 2 percent, per ASTM E77.

Calibration: Degrees F.

DIAL THERMOMETERS

Thermometers - Fixed Mounting: Dial type bimetallic actuated; ASTM E1; stainless steel case, silicone fluid damping, white with black markings and black pointer, hermetically sealed lens, stainless steel stem.

        - Accuracy: 1 percent.

        - Calibration: Degrees F.

Thermometer: ASTM E1, stainless steel case, adjustable angle with front recalibration, bimetallic helix actuated with silicone fluid damping, white with black markings and black pointer hermetically sealed lens, stainless steel stem.

        - Accuracy: 1 percent.

        - Calibration: Degrees F.

STATIC PRESSURE GAUGES

3-1/2 inch (90 mm) diameter dial in metal case, diaphragm actuated, black figures on white background, front recalibration adjustment, 2 percent of full scale accuracy.

PART 3 - EXECUTION

INSTALLATION

Install positive displacement meters with isolating valves on inlet and outlet to AWWA M6. Provide full line size valved bypass with globe valve for liquid service meters.

Provide instruments with scale ranges selected according to service with largest appropriate scale.

  - END OF SECTION  23 05 19