## Sheet1
CALPOLY POINT NAMING STANDARD | [5 empty] | 2019-11-19
EXAMPLE - 171C_C129-HWP1.SPD |  | EXAMPLE - 003_418-AH3.SF.SS | EXAMPLE - 186_ROOF-AH1.SF.SS
171C = BUILDING NUMBER |  | 003 = BUILDING NUMBER | 186 = BUILDING NUMBER
C129 = ROOM NUMBER OR LOCATION |  | 418 = ROOM NUMBER OR LOCATION | ROOF = ROOM NUMBER OR LOCATION
HWP1 = EQUIPMENT |  | AH3 = AIR HANDLER | AH1 = AIR HANDLER
.SPD = SPEED |  | SF = SUPPLY FAN | SF = SUPPLY FAN
|  | .SS = START STOP | .SS = START STOP
Follow the guidelines below:
1. Do not use “V” for virtual in point names for example use .ENA not .VENA
2. Do not use 0-10 volts for the scale of an end device. Use 0-100 PCT
3. Do not add virtual points to table the LOOP output for example
LOOP(0,SAT,CLP,SATS,935,25,0,5,50.0,0.0,100.0,0)
TABLE(CLP,VCHWV,0.0,0.0,100.0,100.0)
TABLE(VCHWV,CHWV,0.0,0.0,100.0,100.0)
TABLE(CLP,CHWV,0.0,0.0,100.0,100.0)
4. Always use capital letters in point names, descriptors and units.
5. Use enhanced alarming for analog points.
FIELD PANEL POINTS
POINT NAME | POINT DESCRIPTOR | DESCRIPTION | UNITS | FORMAT | NOTES
.CDT | COLD DECK TEMP | COLD DECK TEMP | DEG F | FLOAT =1
.CDTS | COLD DECK STPT | COLD DECK SET POINT | DEG F | FLOAT =1
.CHWST | CHW SUP TEMP | CHILLED WATER SUPPLY TEMP | DEG F | FLOAT =1
.CHWSTS | CHW SUP STPT | CHILLED WATER SUPPLY SET POINT | DEG F | FLOAT =1
.CHWRT | CHW RET TEMP | CHILLED WATER RETURN TEMP | DEG F | FLOAT =1
.FLT | FILTER DP |  | IN H2O | FLOAT =1
.HDT | HOT DECK TEMP | HOT DECK TEMP | DEG F | FLOAT =1
.HDTS | HOT DECK STPT | HOT DECK SET POINT | DEG F | FLOAT =1
.HWST | HW SUP TEMP | HOT WATER SUPPLY TEMP | DEG F | FLOAT =1
.HWSTS | HW SUP STPT | HOT WATER SUPPLY SET POINT | DEG F | FLOAT =1
.HWRT | HW RET TEMP | HOT WTER RETURN TEMP | DEG F | FLOAT =1
.DHWST | DHW SUP TEMP | DOMESTIC HOT WATER SUPPLY TEMP | DEG F | FLOAT =1
.DHWSTS | DHW SUP STPT | DOMESTIC HOT WATER SUPPLY SET POINT | DEG F | FLOAT =1
.MAT | MIXED AIR TEMP | MIXED AIR TEMP | DEG F | FLOAT =1
.MATS | MIXED AIR STPT | MIXED AIR STPT | DEG F | FLOAT =1
.OAE | OS AIR ENTHALPY | OUTSIDE AIR ENTHALPY | BTU/LB | INTEGER
.OAH | OS AIR HUMIDITY | OUTSIDE AIR HUMIDITY | PCT | INTEGER
.OAT | OS AIR TEMP | OUTSIDE AIR TEMP | DEG F | FLOAT =1
.OAQ | OS AIR QUALITY | OS AIR QUALITY | PPM | INTEGER
.OAF | OS AIR FLOW | OUTSIDE AIR FLOW | CFM | INTEGER
.RAT | RET AIR TEMP | RETURN AIR TEMP | DEG F | FLOAT =1
.RATS | RET AIR STPT | RETURN AIR SET POINT | DEG F | FLOAT =1
.SAT | SUP AIR TEMP | SUPPLY AIR TEMP | DEG F | FLOAT =1
.SATS | SUP AIR STPT | SUPPLY AIR SET POINT | DEG F | FLOAT =1
.SAF | SUP AIR FLOW | SUPPLY AIR FLOW | CFM | INTEGER
.RMT | ROOM TEMP | ROOM TEMP | DEG F | FLOAT =1
.RMTS | ROOM TEMP STPT | ROOM TEMP STPT | DEG F | FLOAT =1
.RAH | RET AIR HUMIDITY | RETURN AIR HUMIDITY | DEG F | INTEGER
.RAE | RET AIR ENTHALPY | RETURN AIR ENTHALPY | BTU/LB | INTEGER
.RAF | RET AIR FLOW | RETURN AIR FLOW | CFM | INTEGER
.RAQ | RET AIR QUALITY | RETURN AIR QUALITY | PPM | INTEGER
.SAH | SUP AIR HUMIDITY | SUPPLY AIR HUMDITY | PCT | INTEGER
.BSP | BLDG STATIC | BUILDING STATIC PRESSURE | IN H2O | FLOAT =2
.BSPS | BLDG STATIC STPT | BUILDING STATIC PRESSURE SET POINT | IN H2O | FLOAT =2
.DSP | DUCT STATIC | DUCT STATIC | IN H2O | FLOAT =2
.DSPS | DUCT STATIC STPT | DUCT STATIC SET POINT | IN H2O | FLOAT =2
.HW.DP | HW DIFF PRESS | HOT WATER DIFFERENTIAL PRESSURE | PSI | FLOAT =1
.HW.DPS | HW DIFF STPT | HOT WATER DIFFERENTIAL PRESSURE STPT | PSI | FLOAT =1
.CHW.DP | CHW DIFF PRESS | CHILLED WATER DIFFERENTIAL PRESSURE | PSI | FLOAT = 1
.CHW.DPS | CHW DIFF STPT | CHILLED WATER DIFFERENTIAL PRESSURE STPT | PSI | FLOAT =1
.PRS | PRESSURE |  | PSI | FLOAT =1
.HWF | HW FLOW | HOT WATER FLOW | GPM | INTEGER
.HWFS | HW FLOW STPT | HOT WATER FLOW SET POINT | GPM | INTEGER
.CHWF | CHW FLOW | CHILLED WATER FLOW | GPM | INTEGER
.CHWFS | CHW FLOW STPT | CHILLED WATER FLOW SET POINT | GPM | INTEGER
.DWF | DOM WTR FLOW | DOMESTIC WATER FLOW | GPM | INTEGER
.RF.SPD | SPEED COMMAND | RETURN FAN SPEED COMMAND | PCT | INTEGER
.SF.SPD | SPEED COMMAND | SUPPLY FAN SPEED COMMAND | PCT | INTEGER
.EF1.SPD | SPEED COMMAND | EXHAUST FAN SPEED | PCT | INTEGER
.CHWP1.SPD | SPEED COMMAND | CHILLED WATER PUMP SPEED | PCT | INTEGER
.HWP1.SPD | SPEED COMMAND | HOT WATER PUMP SPEED | PCT | INTEGER
.DHWP1.SPD | SPEED COMMAND | DOMESTIC HOT WATER PUMP SPEED | PCT | INTEGER
.BPD | BYPASS DMPR | BYPASS DAMPER
.ID | ISO DAMPER | ISOLATION DAMPER
.SD | SCRUBBER DMPR
.RAD | RET AIR DMPR | RETURN AIR DAMPER | PCT | INTEGER | DEVICES WITH BE SCALED SO
.EAD | EXH AIR DMPR | EXHAUST AIR DAMPER | PCT | INTEGER | 0 PCT = CLOSED,100 PCT = OPEN
.OAD | OS AIR DMPR | OUTSIDE AIR DAMPER | PCT | INTEGER | 0=STOP, 100 = FULL SPEED
.MOAD | MIN OSA DMPR | MINIMUM OUTSIDE AIR DAMPER | PCT | INTEGER
.CHWV | CHW VALVE | CHILLED WATER VALVE | PCT | INTEGER
.HWV | HW VALVE | HOT WATER VALVE | PCT | INTEGER
.DHWV | DOM HW VALVE | DOMESTIC HOT WATER VALVE | PCT | INTEGER
.MAD | MIXED AIR DMPR | MIXED AIR DAMPER -EA,RA AND OA | PCT | INTEGER | 0= 0%OA AND EA 100% RA
.MOSA | MIN OSA POSITION | MINIMUM OSA DAMPER POSITION | PCT | INTEGER
.BLP | LOOP OUTPUT | BUILDING STATIC LOOP OUTPUT | PCT | INTEGER
.SLP | LOOP OUTPUT | STATIC PRESSURE LOOP OUTPUT | PCT | INTEGER
.CLP | LOOP OUTPUT | COOLING LOOP OUTPUT | PCT | INTEGER
.HLP | LOOP OUTPUT | HEATING LOOP OUTPUT | PCT | INTEGER
.MLP | LOOP OUTPUT | MIXED AIR LOOP OUTPUT | PCT | INTEGER
.DHLP | LOOP OUTPUT | DOMESTIC LOOP OUTPUT | PCT | INTEGER
.ALM | ALARM | ANY ALARM
.FAP | FA PURGE | FIRE ALARM PURGE
.EO | EMER OFF | EMERGENCY OFF
.SF.SS | START STOP | SUPPLY FAN START STOP
.RF.SS | START STOP | RETURN FAN START STOP
.EF.SS | START STOP | EXHAUST FAN START STOP
.HWP1.SS | START STOP | HOT WATER PUMP START STOP
.CHWP1.SS | START STOP | CHILLED WATER PUMP START STOP
.DHWP1.SS | START STOP | DOMESTIC HOW WATER PUMP START STOP
.BPV | BYPASS VALVE | PUMP,COOLING TOWER BYPASS
.BPV.OPN | BPV OPEN
.BPV.CLS | BPV CLOSED
.LSP | LO STATIC ALM | LOW STATIC PRESSURE ALARM
.HSP | HI STATIC ALM | HIGH STATIC PRESSURE ALARM
.IV | ISO VALVE
.IV.OPN | ISO OPEN
.IV.CLS | ISO CLOSED
.PRF | PROOF | PROOF POINT
.SSD | SUP SMK DETECTOR | SUPPLY SMOKE DETECTOR
.RSD | RET SMK DETECTOR | RETURN SMOKE DETECTOR
.FFLT | FILTER ALARM | FINAL FILTER ALARM
.RFLT | FILTER ALARM | RETURN FILTER ALARM
.PFLT | FILTER ALARM | PRE FILTER ALARM
.FLT | FILTER ALARM | FILTER ALARM
.TMR | TIMER | TIMER | SEC
.FA | FIRE ALARM
.STA | STATUS | PUMP,FAN,CHILLER,??? STATUS
.SEC | SECONDARY
.ENA | ENABLE | UNIT ENABLE
.ENABLE | ENABLE | UNIT ENABLE
.ECON | ECONOMIZER | ECONOMIZER ENABLE
.MODE | MODE | MODE POINT
.WU | WARM UP MODE | WARM UP MODE
TEC NAMING ON SYSTEM PROFILE
EXAMPLE - 003_AH3-318.VAV | EXAMPLE - 003_AH3-418.FCU
003 = BUILDING NUMBER | 003 = BUILDING NUMBER
AH3 = AIR HANDLER | AH3 = AIR HANDLER
418 = THERMOSTAT LOCATION | 418 = THERMOSTAT LOCATION
VAV = TYPE | FCU = TYPE
.VAV |  | VAV BOX
.FCU |  | FAN COIL UNIT
.LCM |  | LAB CONTROL MODULE
.RPC |  | ROOM PRESSURE CONTROL
.FHC |  | FUME HOOD CONTROLLER
VFD NAMING ON SYSTEM PROFILE
EXAMPLE - 003_418-AH3.SVFD | EXAMPLE - 003_418-HWP1.VFD
003 = BUILDING NUMBER | 003 = BUILDING NUMBER
AH3 = AIR HANDLER | HWP1 = PUMP
418 = AHU LOCATION | 418 = PUMP LOCATION
SVFD = FAN OR PUMP TYPE | VFD
.SVFD | SUPPLY VFD
.RVFD | RETURN VFD
.EVFD | EXHAUST VFD
.VFD | PUMP VFD