- Section 23 11 23 - Facility Natural-Gas Piping

  - PART 1 GENERAL

    - SECTION INCLUDES

      - Pipe, pipe fittings, valves, and connections for natural gas piping systems.

    - RELATED REQUIREMENTS

      - Section 23 05 53 - Identification for HVAC Piping and Equipment.

      - Section 33 52 16 - Gas Hydrocarbon Piping.

    - SUBMITTALS

      - See Section 01 30 00 - Administrative Requirements, for submittal procedures.

      - Product Data: Provide data on pipe materials, pipe fittings, valves, and accessories. Provide manufacturers catalog information. Indicate valve data and ratings.

      - Project Record Documents: Record actual locations of valves.

  - PART 2 PRODUCTS

    - NATURAL GAS PIPING, BURIED BEYOND 5 FEET (1500 mm) OF BUILDING

      - Steel Pipe: ASTM A53/A53M, Schedule 40 black.

        - Fittings: ASTM A234/A234M, wrought steel welding type, with AWWA C105/A21.5 polyethylene jacket or double layer, half-lapped 10 mil (0.25 mm) polyethylene tape.

        - Joints: ASME B31.1, welded.

      - Polyethylene Pipe: ASTM D2513, SDR 11.

        - Fittings: ASTM D2683 or ASTM D2513 socket type.

        - Joints: Fusion welded.

    - NATURAL GAS PIPING, BURIED WITHIN 5 FEET (1500 mm) OF BUILDING

      - Steel Pipe: ASTM A53/A53M, Schedule 40 black.

        - Fittings: ASTM A234/A234M, wrought steel welding type.

        - Joints: ANSI Z223.1, welded.

        - Jacket: AWWA C105/A21.5 polyethylene jacket or double layer, half-lapped 10 mil (0.25 mm) polyethylene tape.

    - NATURAL GAS PIPING, ABOVE GRADE

      - Steel Pipe: ASTM A53/A53M, Schedule 40 black.

        - Fittings: ASME B16.3, malleable iron, or ASTM A234/A234M, wrought steel welding type.

        - Joints: Threaded or welded to ASME B31.1.

    - FLANGES, UNIONS, AND COUPLINGS

      - Unions for Pipe Sizes 3 Inches (80 mm) and Under:

        - Ferrous pipe: Class 150 malleable iron threaded unions.

    - PIPE HANGERS AND SUPPORTS

      - Provide hangers and supports that comply with MSS SP-58.

        - If type of hanger or support for a particular situation is not indicated, select appropriate type using MSS SP-58 recommendations.

        - Overhead Supports: Individual steel rod hangers attached to structure or to trapeze hangers.

        - Trapeze Hangers: Welded steel channel frames attached to structure.

        - Vertical Pipe Support: Steel riser clamp.

    - BALL VALVES

      - Construction, ​4 Inches (100 mm)​ and Smaller: MSS SP-110, Class 150, ​400 psi (2760 kPa)​ CWP, ​bronze or ductile iron​ body, ​304 stainless steel or chrome plated brass​ ball, regular port, Teflon seats and stuffing box ring, blow-out proof stem, lever handle​ with balancing stops​, ​threaded or grooved​ ends​ with union​.

  - PART 3 EXECUTION

    - INSTALLATION

      - Install in accordance with manufacturer's instructions.

      - Pipe Hangers and Supports:

        - Install in accordance with ASME B31.9.

    - SERVICE CONNECTIONS

      - Provide new gas service complete with gas meter and regulators in accordance with Section 33 52 16. Gas service distribution piping to have initial minimum pressure of 7 inch wc (1.75 kPa). Provide regulators on each line serving gravity type appliances, sized in accordance with equipment.

  - END OF SECTION  23 11 23