- Section 23 21 13 - Hydronic Piping

  - PART 1 GENERAL

    - REFERENCE STANDARDS

      - ASME BPVC-IX - Boiler and Pressure Vessel Code, Section IX - Welding, Brazing, and Fusing Procedures; Welders; Brazers; and Welding, Brazing and Fusing Operators 2019.

      - ASME B16.3 - Malleable Iron Threaded Fittings: Classes 150 and 300 2016.

      - ASME B16.18 - Cast Copper Alloy Solder Joint Pressure Fittings 2018.

      - ASME B16.22 - Wrought Copper and Copper Alloy Solder-Joint Pressure Fittings 2018.

      - ASME B31.9 - Building Services Piping 2017.

      - ASTM A53/A53M - Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless 2018.

      - ASTM A234/A234M - Standard Specification for Piping Fittings of Wrought Carbon Steel and Alloy Steel for Moderate and High Temperature Service 2018a.

      - ASTM B32 - Standard Specification for Solder Metal 2008 (Reapproved 2014).

      - ASTM B88 - Standard Specification for Seamless Copper Water Tube 2016.

      - ASTM B88M - Standard Specification for Seamless Copper Water Tube (Metric) 2018.

      - ASTM D1785 - Standard Specification for Poly(Vinyl Chloride) (PVC) Plastic Pipe, Schedules 40, 80, and 120 2015, with Editorial Revision (2018).

      - ASTM D2241 - Standard Specification for Poly (Vinyl Chloride) (PVC) Pressure-Rated Pipe (SDR Series) 2015.

      - ASTM D2466 - Standard Specification for Poly(Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 40 2017.

      - ASTM D2467 - Standard Specification for Poly(Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 80 2015.

      - ASTM D2855 - Standard Practice for the Two-Step (Primer & Solvent Cement) Method of Joining Poly (Vinyl Chloride) (PVC) or Chlorinated Poly (Vinyl Chloride) (CPVC) Pipe and Piping Components with Tapered Sockets 2015.

      - ASTM F1476 - Standard Specification for Performance of Gasketed Mechanical Couplings for Use in Piping Applications 2007 (Reapproved 2013).

      - AWS A5.8M/A5.8 - Specification for Filler Metals for Brazing and Braze Welding 2011 (Amended 2012).

      - AWS D1.1/D1.1M - Structural Welding Code - Steel 2015, with Errata (2016).

      - AWWA C105/A21.5 - Polyethylene Encasement for Ductile-Iron Pipe Systems 2010.

      - AWWA C110/A21.10 - Ductile-Iron and Gray-Iron Fittings 2012.

      - AWWA C111/A21.11 - Rubber-Gasket Joints for Ductile-Iron Pressure Pipe and Fittings 2017.

      - AWWA C151/A21.51 - Ductile-Iron Pipe, Centrifugally Cast 2017, with Errata (2018).

      - AWWA C606 - Grooved and Shouldered Joints 2015.

      - MSS SP-58 - Pipe Hangers and Supports - Materials, Design, Manufacture, Selection, Application, and Installation 2018.

    - QUALITY ASSURANCE

      - Date stamp all castings used for coupling housings, fittings, valve bodies, etc. for quality assurance and traceability.

      - Welder Qualifications: Certify in accordance with ASME BPVC-IX.

  - PART 2 PRODUCTS

    - HYDRONIC SYSTEM REQUIREMENTS

      - Comply with ASME B31.9 and applicable federal, state, and local regulations.

      - Piping: Provide piping, fittings, hangers and supports as required, as indicated, and as follows:

        - Where more than one piping system material is specified, provide joining fittings that are compatible with piping materials and ensure that the integrity of the system is not jeopardized.

        - Use non-conducting dielectric connections whenever jointing dissimilar metals.

        - Grooved mechanical joints may be used in accessible locations only.

          - Accessible locations include those exposed on interior of building, in pipe chases, and in mechanical rooms, aboveground outdoors, and as approved by Architect.

          - Use rigid joints unless otherwise indicated.

        - Provide pipe hangers and supports in accordance with ASME B31.9 or MSS SP-58 unless indicated otherwise.

      - Pipe-to-Valve and Pipe-to-Equipment Connections: Use flanges, unions or grooved couplings to allow disconnection of components for servicing; do not use direct welded, soldered, or threaded connections.

      - Valves: Provide valves where indicated:

      - Welding Materials and Procedures: Conform to ASME BPVC-IX.

    - HEATING WATER AND GLYCOL PIPING, BURIED

      - Steel Pipe: ASTM A53/A53M, Schedule 40, black, with AWWA C105/A21.5 polyethylene jacket, or double layer, half-lapped polyethylene tape.

      - Steel Pipe Sizes 12 inch (305 mm) and Greater: ASTM A53/A53M, 3/8 inch (9.5 mm) wall, black with AWWA C105/A21.5 polyethylene jacket, or double layer, half-lapped polyethylene tape.

        - Fittings: ASTM A234/A234M, wrought steel welding type with double layer, half-lapped polyethylene tape.

        - Joints: Welded in accordance with AWS D1.1/D1.1M.

        - Casing: Closed glass cell insulation.

      - Copper Tube: ASTM B88 (ASTM B88M), Type K (A), annealed.

        - Fittings: ASME B16.22, wrought copper.

        - Joints: Braze, AWS A5.8M/A5.8 BCuP copper/silver alloy.

        - Casing: Closed glass cell insulation.

    - HEATING WATER AND GLYCOL PIPING, ABOVE GRADE

      - Steel Pipe: ASTM A53/A53M, Schedule 40, black, using one of the following joint types:

        - Welded Joints: ASTM A234/A234M, wrought steel welding type fittings; AWS D1.1/D1.1M welded.

        - Threaded Joints: ASME B16.3, malleable iron fittings.

        - Grooved Joints: AWWA C606 grooved pipe, fittings of same material, and mechanical couplings.

      - Steel Pipe Sizes 12 Inch (305 mm) and Greater: ASTM A53/A53M, 3/8 inch (9.5 mm) wall, black, using one of the following joint types:

        - Welded Joints: ASTM A234/A234M, wrought steel welding type fittings; AWS D1.1/D1.1M welded.

        - Grooved Joints: AWWA C606 grooved pipe, fittings of same material, and mechanical couplings.

      - Copper Tube: ASTM B88 (ASTM B88M), Type K (A), drawn, using one of the following joint types:

        - Solder Joints: ASME B16.18 cast brass/bronze or ASME B16.22 solder wrought copper fittings.

          - Solder: ASTM B32 lead-free solder, HB alloy (95-5 tin-antimony) or tin and silver.

          - Braze: AWS A5.8M/A5.8 BCuP copper/silver alloy.

        - Grooved Joints: AWWA C606 grooved tube, fittings of same material, and copper-tube-dimension mechanical couplings.

        - Tee Connections: Mechanically extracted collars with notched and dimpled branch tube.

    - CHILLED WATER PIPING, BURIED

      - Steel Pipe: ASTM A53/A53M, Schedule 40, black with AWWA C105/A21.5 polyethylene jacket, or double layer, half-lapped polyethylene tape.

        - Fittings: ASTM A234/A234M, wrought steel welding type with double layer, half-lapped polyethylene tape.

        - Joints: Welded in accordance with AWS D1.1/D1.1M.

        - Casing: Closed glass cell insulation.

      - Steel Pipe Sizes 12 Inch (305 mm) and Greater: ASTM A53/A53M, 3/8 inch (9.5 mm) wall, black with AWWA C105/A21.5 polyethylene jacket, or double layer, half-lapped polyethylene tape.

        - Fittings: ASTM A234/A234M, wrought steel welding type with double layer, half-lapped polyethylene tape.

        - Joints: Welded in accordance with AWS D1.1/D1.1M.

        - Casing: Closed glass cell insulation.

      - Copper Tube: ASTM B88 (ASTM B88M), Type K (A) annealed.

        - Fittings: ASME B16.22, wrought copper.

        - Joints: Solder, lead free, ASTM B32 HB alloy (95-5 tin-antimony), or tin and silver.

        - Casing: Closed glass cell insulation.

      - Ductile Iron Pipe: AWWA C151/A21.51.

        - Fittings: AWWA C110/A21.10, ductile iron, standard thickness.

        - Joints: AWWA C111/A21.11, Styrene butadiene rubber (SBR) or vulcanized SBR gasket with 3/4 inch (19 mm) diameter rods.

      - PVC Pipe Sizes 6 inch (150 mm) and Smaller: ASTM D1785, Schedule 40, or ASTM D2241, SDR 21 or 26.

        - Fittings: ASTM D2466, or ASTM D2467, PVC.

        - Joints: Solvent welded in accordance with ASTM D2855.

      - PVC Pipe Sizes 8 Inch (200 mm) and Larger: ASTM D1785, Schedule 80, or ASTM D2241, SDR 21 or 26.

        - Fittings: ASTM D2466, or ASTM D2467, PVC.

        - Joints: Solvent welded in accordance with ASTM D2855.

    - CHILLED WATER PIPING, ABOVE GRADE

      - Steel Pipe: ASTM A53/A53M, Schedule 40, black; using one of the following joint types:

        - Welded Joints: ASTM A234/A234M, wrought steel welding type fittings; AWS D1.1/D1.1M welded.

        - Threaded Joints: ASME B16.3, malleable iron fittings.

        - Grooved Joints: AWWA C606 grooved pipe, fittings of same material, and mechanical couplings.

      - Steel Pipe Sizes 12 Inch (305 mm) and Greater: ASTM A53/A53M, 3/8 inch (9.5 mm) wall, black; using one of the following joint types:

        - Welded Joints: ASTM A234/A234M, wrought steel welding type fittings; AWS D1.1/D1.1M welded.

        - Grooved Joints: AWWA C606 grooved pipe, fittings of same material, and mechanical couplings.

      - Copper Tube: ASTM B88 (ASTM B88M), Type K (A), hard drawn; using one of the following joint types:

        - Solder Joints: ASME B16.18 cast brass/bronze or ASME B16.22, solder wrought copper fittings.

          - Solder: ASTM B32 lead-free solder, HB alloy (95-5 tin-antimony) or tin and silver.

        - Grooved Joints: AWWA C606 grooved tube, fittings of same material, and copper-tube-dimension mechanical couplings.

        - Tee Connections: Mechanically extracted collars with notched and dimpled branch tube.

      - PVC Pipe: ASTM D1785, Schedule 40, or ASTM D2241, SDR 21 or 26.

        - Fittings: ASTM D2466 or ASTM D2467, PVC.

        - Joints: Solvent welded in accordance with ASTM D2855.

      - PVC Pipe Sizes 8 Inch (203 mm) and Larger: ASTM D1785, Schedule 80, or ASTM D2241, SDR 21 or 26.

        - Fittings: ASTM D2466 or ASTM D2467, PVC.

        - Joints: Solvent welded in accordance with ASTM D2855.

    - CONDENSER WATER PIPING, BURIED

      - Steel Pipe: ASTM A53/A53M, Schedule 40, black with AWWA C105/A21.5 polyethylene jacket, or double layer, half-lapped polyethylene tape.

        - Fittings: ASTM A234/A234M, wrought steel welding type with double layer, half-lapped polyethylene tape.

        - Joints: Threaded for pipe 2 inch (50 mm) and under; AWS D1.1/D1.1M, welded for pipe over 2 inch (50 mm).

      - Steel Pipe Sizes 12 Inch (305 mm) and Greater: ASTM A53/A53M, 3/8 inch (9.5 mm) wall, black with AWWA C105/A21.5 polyethylene jacket, or double layer, half-lapped polyethylene tape.

        - Fittings: ASTM A234/A234M, wrought steel welding type with double layer, half-lapped polyethylene tape.

        - Joints: Welded in accordance with AWS D1.1/D1.1M.

      - Copper Tube: ASTM B88 (ASTM B88M), Type K (A) annealed.

        - Fittings: ASME B16.22, wrought copper.

        - Joints: Solder, lead free, 95-5 tin-antimony, or tin and silver.

      - Ductile Iron Pipe: AWWA C151/A21.51.

      - PVC Pipe: ASTM D1785, Schedule 40, or ASTM D2241, SDR 21 or 26.

        - Fittings: ASTM D2466 or ASTM D2467, PVC.

        - Joints: Solvent welded in accordance with ASTM 2855.

      - PVC Pipe sizes 8 inch (200 mm) and larger: ASTM D1785, Schedule 80, or ASTM D2241, SDR 21 or 26.

        - Fittings: ASTM D2466 or ASTM D2467, PVC.

        - Joints: Solvent welded in accordance with ASTM D2855.

    - CONDENSER WATER PIPING, ABOVE GRADE

      - Steel Pipe: ASTM A53/A53M, Schedule 40, black.

        - Welded Joints: ASTM A234/A234M, wrought steel welding type fittings with finish matching piping; AWS D1.1/D1.1M welded.

        - Threaded Joints: ASME B16.3, malleable iron fittings with finish matching piping.

        - Grooved Joints: AWWA C606 grooved pipe, fittings of same material, and mechanical couplings.

      - Steel Pipe Sizes 12 Inch (305 mm) and Greater: ASTM A53/A53M, 3/8 inch (9.5 mm) wall, black; using one of the following joint types:

        - Welded Joints: ASTM A234/A234M, wrought steel welding type fittings; AWS D1.1/D1.1M welded.

        - Grooved Joints: AWWA C606 grooved pipe, fittings of same material, and mechanical couplings.

      - Copper Tube: ASTM B88 (ASTM B88M), Type K (A), drawn; using one of the following joint types:

        - Solder Joints: ASME B16.18 cast brass/bronze or ASME B16.22 solder wrought copper fittings.

          - Solder: ASTM B32 lead-free solder, HB alloy (95-5 tin-antimony) or tin and silver.

        - Grooved Joints: AWWA C606 grooved tube, fittings of same material, and copper-tube-dimension mechanical couplings.

        - Tee Connections: Mechanically extracted collars with notched and dimpled branch tube.

      - PVC Pipe: ASTM D1785, Schedule 40, or ASTM D2241, SDR 21 or 26.

        - Fittings: ASTM D2466 or ASTM D2467, PVC.

        - Joints: Solvent welded in accordance with ASTM D2855.

      - PVC Pipe Sizes 8 Inch (200 mm) and Greater: ASTM D1785, Schedule 80, or ASTM D2241, SDR 21 or 26.

        - Fittings: ASTM D2466 or ASTM D2467, PVC.

        - Joints: Solvent welded in accordance with ASTM D2855.

    - RADIANT HEATING PIPING

      - Copper Tube: ASTM B88 (ASTM B88M), Type K (A) annealed.

        - Fittings: ASME B16.22, wrought copper.

        - Joints: Braze, AWS A5.8M/A5.8 BCuP copper/silver alloy.

    - PIPE HANGERS AND SUPPORTS

      - Provide hangers and supports that comply with MSS SP-58.

        - If type of hanger or support for a particular situation is not indicated, select appropriate type using MSS SP-58 recommendations.

      - In grooved installations, use rigid couplings with offsetting angle-pattern bolt pads or with wedge shaped grooves in header piping to permit support and hanging in accordance with ASME B31.9.

    - UNIONS, FLANGES, MECHANICAL COUPLINGS, AND DIELECTRIC CONNECTIONS

      - Unions for Pipe 2 Inches (50 mm) and Less:

      - Flanges for Pipe 2 Inches (50 mm) and Greater:

      - Mechanical Couplings for Grooved and Shouldered Joints: Two or more curved housing segments with continuous key to engage pipe groove, circular C-profile gasket, and bolts to secure and compress gasket.

        - Dimensions and Testing: In accordance with AWWA C606.

        - Mechanical Couplings: Comply with ASTM F1476.

        - Bolts and Nuts: Hot dipped galvanized or zinc-electroplated steel.

        - When pipe is field grooved, provide coupling manufacturer's grooving tools.

  - PART 3 EXECUTION

    - INSTALLATION

      - Install in accordance with manufacturer's instructions.

      - PVC Pipe: Make solvent-welded joints in accordance with ASTM D2855.

      - Route piping in orderly manner, parallel to building structure, and maintain gradient.

      - Install piping to conserve building space and to avoid interfere with use of space.

      - Group piping whenever practical at common elevations.

      - Slope piping and arrange to drain at low points.

  - END OF SECTION  23 21 13