- Section 23 25 00 - HVAC Water Treatment

  - PART 1 GENERAL

    - SECTION INCLUDES

      - By-pass (pot) feeder.

      - Drip feeder.

      - Solution metering pump.

      - Solution tanks.

      - Agitator.

      - Liquid level switch.

      - Conductivity controller.

      - Water meter.

      - Solenoid valves.

      - Test equipment.

    - RELATED REQUIREMENTS

      - Section 23 09 13 - Instrumentation and Control Devices for HVAC.

      - Section 23 21 13 - Hydronic Piping.

    - REFERENCE STANDARDS

      - UL (DIR) - Online Certifications Directory Current Edition.

    - SUBMITTALS

      - Product Data: Provide chemical treatment materials, chemicals, and equipment including electrical characteristics and connection requirements.

      - Shop Drawings: Indicate system schematic, equipment locations, and controls schematics, electrical characteristics and connection requirements.

  - PART 2 PRODUCTS

    - REGULATORY REQUIREMENTS

      - Comply with applicable codes for addition of non-potable chemicals to building mechanical systems and to public sewage systems.

      - Comply with UL (DIR) requirements.

      - Provide certificate of compliance from Authority Having Jurisdiction indicating approval of installation.

    - BY-PASS (POT) FEEDER

      - 2 quart (1.9 L) quick opening cap for working pressure of 175 psi (1200 kPa).

    - DRIP FEEDER

      - Plastic reservoir with coil of capillary tubing with probe, weight, charging syringe, and clip.

    - SOLUTION METERING PUMP

      - Positive displacement, diaphragm pump with adjustable flow rate, thermoplastic construction, continuous-duty fully enclosed electric motor and drive, and built-in relief valve.

    - SOLUTION TANKS

      - 30 gallon (114 L) capacity, polyethylene, self-supporting, 1 gallon (3.8 L) graduated markings; molded fiberglass cover with recess for mounting pump, agitator, and liquid level switch.

    - AGITATOR

      - Totally enclosed electric motor, cast iron clamp and motor mount, 1/2 inch (13 mm) diameter coated Type 316 stainless steel propeller.

    - LIQUID LEVEL SWITCH

      - Polypropylene housing with integrally mounted PVC air trap, receptacles for connection to metering pump, and low level alarm.

    - CONDUCTIVITY CONTROLLER

      - Packaged monitor controller with solid state circuiting, five percent accuracy, linear dial adjustment, built-in calibration switch, on-off switch and light, control function light, output to control circuit and recorder.

    - WATER METER

      - Displacement type cold water meter with sealed, tamper-proof magnetic drive, impulse contact register, single pole, double throw dry contact switch.

    - SOLENOID VALVES

      - Forged brass body globe pattern, normally open or closed as required, explosion-proof and watertight solenoid enclosure, and continuous duty coil.

    - TEST EQUIPMENT

      - Provide white enamel test cabinet with local and fluorescent light, capable of accommodating 4 - 10 ml zeroing titrating burettes and associated reagents.

  - END OF SECTION  23 25