- Section 23 74 13 - Packaged Outdoor Central-Station Air-Handling Units

  - PART 2 PRODUCTS

    - MANUFACTURED UNITS

      - General: Roof mounted units having gas burner and electric refrigeration.

      - Description: Self-contained, packaged, factory assembled and prewired, consisting of cabinet and frame, supply fan, return fan, heat exchanger and burner, heat recovery coil, controls, air filters, refrigerant cooling coil and compressor, condenser coil and condenser fan.

    - FABRICATION

      - Cabinet: Steel with baked enamel finish, including access panels with screwdriver operated flush cam type fasteners. Structural members shall be minimum 18 gage, 0.0478 inch (1.21 mm), with access doors or panels of minimum 20 gage, 0.0359 inch (0.91 mm).

      - Heat Exchangers: Aluminized steel, of welded construction.

      - Supply​ and Return​ Fan: Forward curved centrifugal type, resiliently mounted with V-belt drive, ​adjustable variable pitch motor pulley, ​and rubber isolated hinge mounted​ high efficiency​ motor​ or direct drive as indicated​.​ [____] . ​Refer to Section ​22 05 48​.

    - BURNER

      - Gas Burner: Atmospheric type burner with adjustable combustion air supply, pressure regulator, gas valves, manual shut-off, intermittent spark or glow coil ignition, flame sensing device, and automatic 100 percent shut-off pilot.

      - Gas Burner Safety Controls: Energize ignition, limit time for establishment of flame, prevent opening of gas valve until pilot flame is proven, stop gas flow on ignition failure, energize blower motor, and after air flow proven and slight delay, allow gas valve to open.

    - EVAPORATOR COIL

      - Provide copper tube aluminum fin coil assembly with galvanized drain pan and connection.

      - Provide capillary tubes or thermostatic expansion valves for units of 6 tons (21 kw) capacity and less, and thermostatic expansion valves and alternate row circuiting for units 7.5 tons (26 kw) cooling capacity and larger.

    - COMPRESSOR

      - Provide hermetic compressors, 3600 rpm maximum, resiliently mounted with positive lubrication, crankcase heater, high and low pressure safety controls, motor overload protection, suction and discharge service valves and gauge ports, and filter drier.

    - CONDENSER COIL

      - Provide copper tube aluminum fin coil assembly with subcooling rows and coil guard.

      - Provide direct drive propeller fans, resiliently mounted with fan guard, motor overload protection, wired to operate with compressor. Provide high efficiency fan motors.

    - HEAT RECOVERY COIL

      - Provide copper tube aluminum fin coil assembly with multiple circuits arranged to provide heat recovery.

  - END OF SECTION  23 74 13