SECTION 26 24 16 600V PANELBOARDS

PART 1 - GENERAL

SUMMARY

This Section includes load centers and panelboards, overcurrent protective devices, and associated auxiliary equipment rated 600 V and less for the following types:

Lighting and appliance branch-circuit panelboards.

Distribution panelboards.

Transient voltage surge suppressor panelboards.

B. Related Sections include the following:

Division 26 Section "Seismic Controls for Electrical Work."

DEFINITIONS

EMI:  Electromagnetic interference.

GFCI:  Ground-fault circuit interrupter.

RMS:  Root mean square.

SPDT:  Single pole, double throw.

SUBMITTALS

Product Data:  For each type of panelboard, overcurrent protective device, and component indicated.  Include dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, and finishes.

Shop Drawings:  For each panelboard and related equipment.

Dimensioned plans, elevations, sections, and details.  Show tabulations of installed devices, equipment features, and ratings.  Include the following:

Enclosure types and details for types other than NEMA 250, Type 1.

Bus configuration, current, and voltage ratings.

Short-circuit current rating of panelboards and overcurrent protective devices.

UL listing for series rating of installed devices.

Features, characteristics, ratings, and factory settings of individual overcurrent protective devices and auxiliary components.

Wiring Diagrams:  Diagram power, signal, and control wiring and differentiate between manufacturer-installed and field-installed wiring.

Manufacturer Seismic Qualification Certification:  Submit certification that panelboards, overcurrent protective devices, accessories, and components will withstand seismic forces defined in Division 26 Section "Seismic Controls for Electrical Work."  Include the following:

Basis of Certification:  Indicate whether withstand certification is based on actual test of assembled components or on calculation.

The term "withstand" means "the unit will remain in place without separation of internal and external parts during a seismic event and the unit will be fully operational after the event."

Dimensioned Outline Drawings of Equipment Unit:  Identify center of gravity and locate and describe mounting and anchorage provisions.

Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Field Test Reports:  Submit written test reports and include the following:

Test procedures used.

Test results that comply with requirements.

Results of failed tests and corrective action taken to achieve test results that comply with requirements.

Panelboard Schedules:  For installation in panelboards.  Submit final versions after load balancing.

Maintenance Data:  For panelboards and components to include in maintenance manuals specified in Division 1.  In addition, include the following:

Manufacturer's written instructions for testing and adjusting overcurrent protective devices.

Time-current curves, including selectable ranges for each type of overcurrent protective device.

QUALITY ASSURANCE

Testing Agency Qualifications:  In accordance with Section 26 05 53.

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to Owner, and marked for intended use.

Comply with NEMA PB 1.

Comply with NFPA 70.

COORDINATION

Coordinate layout and installation of panelboards and components with other construction that penetrates walls or is supported by them, including electrical and other types of equipment, raceways, piping, and encumbrances to workspace clearance requirements.

EXTRA MATERIALS

Keys:  Six spares of each type of panelboard cabinet lock, keyed alike to match the Owner standard key requirements.

PART 2 - PRODUCTS

MANUFACTURERS

Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Panelboards, Overcurrent Protective Devices, Controllers, Contactors, and Accessories:

Eaton Corp.; Cutler-Hammer Products.

General Electric Co.; Electrical Distribution & Control Div.

Siemens Energy & Automation, Inc.

Square D Co.

FABRICATION AND FEATURES

Enclosures:  Flush- and surface-mounted cabinets.  NEMA PB 1, Type 1, to meet environmental conditions at installed location.

Outdoor Locations:  NEMA 250, Type 3R.

Kitchen Areas:  NEMA 250, Type 4X, stainless steel.

Other Wet or Damp Indoor Locations:  NEMA 250, Type 4.

Hazardous Areas Indicated on Drawings:  NEMA 250, Type 7C.

Hinged Front Cover:  Entire front trim hinged to box and with standard door within hinged trim cover.

Finish:  Manufacturer's standard enamel finish over corrosion-resistant treatment or primer coat.

Directory Card:  Typed panel circuit schedule/index with transparent protective cover, mounted inside metal frame, inside panelboard door.

Bus:  Hard-drawn copper, 98 percent conductivity.

Main and Neutral Lugs:  Compression type suitable for use with conductor material.

Equipment Ground Bus:  Adequate for feeder and branch-circuit equipment ground conductors; bonded to box.  When isolated grounds are required, provide ground bus insulated from box.

Future Devices:  Mounting brackets, bus connections, and necessary appurtenances required for future installation of devices.

Isolated Equipment Ground Bus:  Adequate for branch-circuit equipment ground conductors; insulated from box.

Extra-Capacity Neutral Bus:  Neutral bus rated 200 percent of phase bus and UL listed as suitable for nonlinear loads.

Split Bus:  Vertical buses divided into individual vertical sections.

Gutter Barrier:  Arrange to isolate individual panel sections.

Column-Type Panelboards:  Narrow gutter extension, with cover, to overhead junction box equipped with ground and neutral terminal buses.

PANELBOARD SHORT-CIRCUIT RATING

UL label indicating series-connected rating with integral or remote upstream devices.  Include size and type of upstream device allowable, branch devices allowable, and UL series-connected short-circuit rating.

Fully rated to interrupt symmetrical short-circuit current available at terminals.

LIGHTING AND APPLIANCE BRANCH-CIRCUIT PANELBOARDS

Branch Overcurrent Protective Devices:  Bolt-on circuit breakers, replaceable without disturbing adjacent units.

Doors:  Front mounted with concealed hinges; secured with flush latch with tumbler lock; keyed alike.

DISTRIBUTION PANELBOARDS

Doors:  Front mounted, except omit in fused-switch panelboards; secured with vault-type latch with tumbler lock; keyed alike.

Main Overcurrent Protective Devices:  Molded Case Circuit Breaker

Branch overcurrent protective devices shall be one of the following:

For Circuit-Breaker Frame Sizes 125 A and Smaller:  Bolt-on circuit breakers.

For Circuit-Breaker Frame Sizes Larger Than 125 A:  Bolt-on circuit breakers; plug-in circuit breakers where individual positive-locking device requires mechanical release for removal.

Fused switches.

OVERCURRENT PROTECTIVE DEVICES

Molded-Case Circuit Breaker:  NEMA AB 1, with interrupting capacity to meet available fault currents.

Thermal-Magnetic Circuit Breakers:  Inverse time-current element for low-level overloads, and instantaneous magnetic trip element for short circuits.  Adjustable magnetic trip setting for circuit-breaker frame sizes 225A and larger.

Adjustable Instantaneous-Trip Circuit Breakers:  Magnetic trip element with front-mounted, field-adjustable trip setting.

Electronic Trip Unit Circuit Breakers:  RMS sensing; field-replaceable rating plug; with the following field-adjustable settings:

Instantaneous trip.

Long- and short-time pickup levels.

Long- and short-time time adjustments.

Ground-fault pickup level, time delay, and I2t response.

Current-Limiting Circuit Breakers:  Frame sizes 400 A and smaller; let-through ratings less than NEMA FU 1, RK-5.

Integrally Fused Circuit Breakers:  Thermal-magnetic trip element with integral limiter-style fuse listed for use with circuit breaker; trip activation on fuse opening or on opening of fuse compartment door.

GFCI Circuit Breakers:  Single- and two-pole configurations with 5 -mA trip sensitivity.

Molded-Case Circuit-Breaker Features and Accessories.  Standard frame sizes, trip ratings, and number of poles.

Lugs:  Compression style, suitable for number, size, trip ratings, and material of conductors.

Application Listing:  Appropriate for application; Type SWD for switching fluorescent lighting loads; Type HACR for heating, air-conditioning, and refrigerating equipment.

Ground-Fault Protection:  Integrally mounted or Remote-mounted relay and trip unit with adjustable pickup and time-delay settings, push-to-test feature, and ground-fault indicator.

Communication Capability:  Circuit-breaker-mounted communication module with functions and features compatible with power monitoring and control system.

Shunt Trip:  120-V trip coil energized from separate circuit, set to trip at 75 percent of rated voltage.

Under-voltage Trip:  Set to operate at 35 to 75 percent of rated voltage without intentional time delay.

Auxiliary Switch:  Two SPDT switches with "a" and "b" contacts; "a" contacts mimic circuit-breaker contacts, "b" contacts operate in reverse of circuit-breaker contacts.

Key Interlock Kit:  Externally mounted to prohibit circuit-breaker operation; key shall be removable only when circuit breaker is in off position.

Zone-Selective Interlocking:  Integral with electronic trip unit; for interlocking ground-fault protection function.

PART 3 - EXECUTION

INSTALLATION

Install panelboards and accessories according to NEMA PB 1.1.

Comply with mounting and anchoring requirements specified in Division 26 Section "Seismic Controls for Electrical Work."

Mounting Heights:  Top of trim 74 inches above finished floor, unless otherwise indicated.

Mounting:  Plumb and rigid without distortion of box.  Mount recessed panelboards with fronts uniformly flush with wall finish.

Circuit Directory:  Create a directory to indicate installed circuit loads after balancing panelboard loads.  Obtain approval before installing.  Use a computer or typewriter to create directory; handwritten directories are not acceptable.

Install filler plates in unused spaces.

Provision for Future Circuits at Flush Panelboards:  Stub four 1-inch empty conduits from panelboard into accessible ceiling space or space designated to be ceiling space in the future.  Stub four 1-inch empty conduits into raised floor space or below slab not on grade.

Wiring in Panelboard Gutters:  Arrange conductors into groups and bundle and wrap with wire ties after completing load balancing.

IDENTIFICATION

Identify field-installed conductors, interconnecting wiring, and components; provide warning signs as specified in Division 26 Section 26 05 33.

Panelboard Nameplates:  Label each panelboard with laminated-plastic nameplate mounted with corrosion-resistant screws.

CONNECTIONS

Install equipment grounding connections for panelboards with ground continuity to main electrical ground bus.

Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

FIELD QUALITY CONTROL

Prepare for acceptance tests as follows:

Test insulation resistance for each panelboard bus, component, connecting supply, feeder, and control circuit.

Test continuity of each circuit.

Testing:  After installing panelboards and after electrical circuitry has been energized, demonstrate product capability and compliance with requirements.

Procedures:  Perform each visual and mechanical inspection and electrical test indicated in NETA ATS, Section 7.5 for switches and Section 7.6 for molded-case circuit breakers.  Certify compliance with test parameters.

Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

Balancing Loads:  After Substantial Completion, but not more than 60 days after Final Acceptance, measure load balancing and make circuit changes as follows:

Measure as directed during period of normal system loading.

Perform load-balancing circuit changes outside normal occupancy/working schedule of the facility and at time directed.  Avoid disrupting critical 24-hour services such as fax machines and on-line data-processing, computing, transmitting, and receiving equipment.

After circuit changes, re-check loads during normal load period.  Record all load readings before and after changes and submit test records.

Tolerance:  Difference exceeding 20 percent between phase loads, within a panelboard, is not acceptable.  Rebalance and recheck as necessary to meet this minimum requirement.

Infrared Scanning:  After Substantial Completion, but not more than 60 days after Final Acceptance, perform an infrared scan of each panelboard.  Remove panel fronts so joints and connections are accessible to portable scanner.

Follow-up Infrared Scanning:  Perform an additional follow-up infrared scan of each panelboard 11 months after date of Substantial Completion.

Instrument:  Use an infrared scanning device designed to measure temperature or to detect significant deviations from normal values.  Provide calibration record for device.

Record of Infrared Scanning:  Prepare a certified report that identifies panelboards checked and describes scanning results.  Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

ADJUSTING

Set field-adjustable switches and circuit-breaker trip ranges.

CLEANING

On completion of installation, inspect interior and exterior of panelboards.  Remove paint splatters and other spots.  Vacuum dirt and debris; do not use compressed air to assist in cleaning.  Repair exposed surfaces to match original finish.

END OF SECTION 26 24 16