26 27 26 – WIRING DEVICES

  - PART 1 - GENERAL

SECTION INCLUDES:

      - Single and duplex receptacles, ground-fault circuit interrupters, integral surge suppression units, and isolated-ground receptacles.

      - Single- and double-pole snap switches and dimmer switches.

      - Device wall plates.

      - Pin and sleeve connectors and receptacles.

      - Floor service outlets, poke-through assemblies, service poles, and multi-outlet assemblies.

RELATED WORK SPECIFIED ELSEWHERE:

      - Identification: Section 26 05 53

      - Conductors: Section 26 05 19

      - Boxes: Section 16130

DEFINITIONS:

      - EMI:  Electromagnetic interference.

      - GFCI:  Ground-fault circuit interrupter.

      - PVC:  Polyvinyl chloride.

      - RFI:  Radio-frequency interference.

      - TVSS:  Transient voltage surge suppressor.

      - UTP:  Unshielded twisted pair.

SUBMITTALS:

      - Product Data:  For each type of product indicated.

      - Field quality-control test reports.

QUALITY ASSURANCE

      - Source Limitations:  Obtain each type of wiring device through one source from a single manufacturer.

      - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

      - Comply with NFPA 70.

  - PART 2 – PRODUCTS

MANUFACTURERS

      - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

        - Wiring Devices:

          - Bryant Electric, Inc./Hubbell Subsidiary.

          - Hubbell Incorporated; Wiring Device-Kellems.

          - Leviton Mfg. Company Inc.

          - Pass & Seymour/Legrand; Wiring Devices Div.

        - Wiring Devices for Hazardous (Classified) Locations:

          - Crouse-Hinds/Cooper Industries, Inc.; Arrow Hart Wiring Devices.

          - EGS/Appleton Electric Company.

          - Killark Electric Manufacturing Co./Hubbell Incorporated.

        - Multi-outlet Assemblies:

          - Hubbell Incorporated; Wiring Device-Kellems.

          - Wiremold Company (The).

        - Poke-Through, Floor Service Outlets and Telephone/Power Poles:

          - Hubbell Incorporated; Wiring Device-Kellems.

          - Pass & Seymour/Legrand; Wiring Devices Div.

          - Square D/Groupe Schneider NA.

          - Thomas & Betts Corporation.

          - Wiremold Company (The).

RECEPTACLES

      - Straight-Blade-Type Receptacles:  Comply with NEMA WD 1, NEMA WD 6, DSCC W-C-596G, and UL 498.  “Decora or style line” type in white color.

      - Straight-Blade and Locking Receptacles:  Heavy -Duty/Industrial grade.

      - Straight-Blade Receptacles:  Hospital grade/Institutional grade.

      - GFCI Receptacles:  Straight blade, feed -through type, Heavy-Duty/Industrial grade, with integral NEMA WD 6, Configuration 5-20R duplex receptacle; complying with UL 498and UL 943.  Design units for installation in a 2-3/4-inch deep outlet box without an adapter.

      - Isolated-Ground Receptacles:  Straight blade, Heavy-Duty/Industrial grade, duplex receptacle, with equipment grounding contacts connected only to the green rounding screw terminal of the device and with inherent electrical isolation from mounting strap.

        - Devices:  Listed and labeled as isolated-ground receptacles.

        - Isolation Method:  Integral to receptacle construction and not dependent on removable parts.

      - TVSS Receptacles:  Straight blade, NEMA WD 6, Configuration 5-20R, with integral TVSS in line to ground, line to neutral, and neutral to ground.

        - TVSS Components:  Multiple metal-oxide varistors; with a nominal clamp level rating of 500 volts and minimum single transient pulse energy dissipation of 140 J line to neutral, and 70 J line to ground and neutral to ground.

        - Active TVSS Indication:  Visual and audible with light visible in face of device to indicate device is "active" or "no longer in service."

        - Receptacle Type:  Hospital grade, with isolated-ground terminal.

        - Identification:  Distinctive marking on face of device to denote TVSS-type unit.

      - Industrial Heavy-Duty Pin and Sleeve Devices:  Comply with IEC 309-1.

      - Hazardous (Classified) Location Receptacles:  Comply with NEMA FB 11.

PENDANT CORD/CONNECTOR DEVICES

      - Description:  Matching, locking-type plug and receptacle body connector, NEMA WD 6, Configurations L5-20P and L5-20R, Heavy-Duty grade.

        - Body:  Nylon with screw-open cable-gripping jaws and provision for attaching external cable grip.

CORD AND PLUG SETS

      - Description:  Match voltage and current ratings and number of conductors to requirements of equipment being connected.

        - Cord:  Rubber-insulated, stranded-copper conductors, with Type SOW-A jacket; with green-insulated grounding conductor and equipment-rating ampacity plus a minimum of 30 percent.

        - Plug:  Nylon body and integral cable-clamping jaws.  Match cord and receptacle type for connection.

SWITCHES

      - Single- and Double-Pole Switches:  Comply with DSCC W-C-896F and UL 20.

      - Snap Switches:  Heavy -Duty grade, quiet type.

      - Dimmer Switches:  Modular, full-wave, solid-state units with integral, quiet on/off switches and audible frequency and EMI/RFI filters.

        - Control:  Continuously adjustable slider; with single-pole or three-way switching to suit connections.

        - Incandescent Lamp Dimmers:  Modular, 120 V, 60 Hz with continuously adjustable, or slider; single pole with soft tap or other quiet switch; EMI/RFI filter to eliminate interference; and 5-inch wire connecting leads.

        - Use fluorescent lamp dimmer switches below with compatible dimming-type ballasts.  Coordinate with Division 16 Section "Interior Lighting."  Use uniform ballast and lamp types to obtain consistent dimming characteristics.

        - Fluorescent Lamp Dimmer Switches:  Modular; compatible with dimmer ballasts; trim potentiometer to adjust low-end dimming; dimmer-ballast combination capable of consistent dimming with low end not greater than 10 percent of full brightness and 1 percent in areas where projection equipment is utilized.

WALL PLATES

      - Single and combination types to match corresponding wiring devices.

        - Plate-Securing Screws:  Metal with head color to match plate finish.

        - Material for Finished Spaces:  0.035-inch- thick, satin-finished stainless steel.

        - Material for Unfinished Spaces:  Smooth, high-impact thermoplastic.

        - Material for Wet Locations:  Cast aluminum with spring-loaded lift cover, with gasket between box and plate, and listed and labeled for use in "wet locations."

FLOOR SERVICE FITTINGS

      - Type:  Modular, flush-type, dual-service units suitable for wiring method used.

      - Compartments:  Barrier separates power from voice and data communication cabling.

      - Service Plate:  Round, die-cast aluminum with satin finish.

      - Power Receptacle:  NEMA WD 6, Configuration 5-20R, gray finish, unless otherwise indicated.

      - Voice and Data Communication Outlet:  Blank cover with bushed cable opening, Two modular, keyed, color-coded, RJ-45 Category 3 jacks for UTP cable or Two modular, keyed, color-coded, RJ-45 Category 5 jacks for UTP cable.

POKE-THROUGH ASSEMBLIES

      - Description:  Factory-fabricated and -wired assembly of below-floor junction box with multi-channeled, through-floor raceway/firestop unit and detachable matching floor service outlet assembly.

        - Service Outlet Assembly:  Pedestal type with services indicated, Flush type with two simplex receptacles and space for two RJ-45 jacks or Flush type with four simplex receptacles and space for four RJ-45 jacks.

        - Size:  Selected to fit nominal 4-inch cored holes in floor and matched to floor thickness.

        - Fire Rating:  Unit is listed and labeled for fire rating of floor-ceiling assembly.

        - Closure Plug:  Arranged to close unused 4-inch cored openings and reestablish fire rating of floor.

        - Wiring Raceways and Compartments:  For a minimum of four No. 12 AWG conductors; and a minimum of 4-pair, Category 5 voice and data communication cables.

MULTI-OUTLET

      - Components of Assemblies:  Products from a single manufacturer designed for use as a complete, matching assembly of raceways and receptacles.

      - Raceway Material: Base, cover and end plates shall be constructed of extruded aluminum #6063-T5, 0.060-inch minimum wall thickness.  Finish shall be clear anodized #AA-C22A31, Class 2.

      - Wire:  No. 12 AWG.

SERVICE POLES

      - Description:  Factory-assembled and -wired units to extend power and voice and data communication from distribution wiring concealed in ceiling to devices or outlets in pole near floor.

        - Poles:  Nominal 2.5-inch- square cross section, with height adequate to extend from floor to at least 6 inches above ceiling, and with separate channels for power wiring and voice and data communication cabling.

        - Mounting:  Ceiling trim flange with concealed bracing arranged for positive connection to ceiling supports; with pole foot and carpet pad attachment.

        - Specify final finish in first subparagraph below if known.

        - Finishes:   Clear anodized #AA-C22A31, Class 2.

        - Wiring:  Sized for minimum of five No. 12 AWG power and ground conductors; and a minimum of four, 4-pair, Category 5 voice and data communication cables.

        - Power Receptacles:  Two duplex, 20-A, heavy-duty, NEMA WD 6, Configuration 5-20R units.

        - Voice and Data Communication Outlets:  Four RJ-45 Category 5 jacks.

FINISHES

      - Color:

        - Wiring Devices Connected to Normal Power System:  Gray as selected by the University, unless otherwise indicated or required by NFPA 70.

        - Wiring Devices Connected to Emergency Power System:  Red.

        - TVSS Devices:  Blue.

        - Isolated-Ground Receptacles:  As specified above, with orange triangle on face.

  - PART 3 - EXECUTION

INSTALLATION

      - Install devices and assemblies level, plumb, and square with building lines.

      - Install wall dimmers to achieve indicated rating after derating for ganging according to manufacturer's written instructions.

      - Install unshared neutral conductors on line and load side of dimmers according to manufacturers' written instructions.

      - Arrangement of Devices:  Unless otherwise indicated, mount flush, with long dimension vertical, and with grounding terminal of receptacles on top.  Group adjacent switches under single, multi-gang wall plates.

      - Remove wall plates and protect devices and assemblies during painting.

      - Adjust locations of floor service outlets and service poles to suit arrangement of partitions and furnishings.

IDENTIFICATION

      - Comply with Section 26 05 53 “Tests and Identifications”.

        - Receptacles:  Identify panelboard and circuit number from which served.  Use hot, stamped or engraved machine printing with black-filled lettering on face of plate, and durable wire markers or tags inside outlet boxes.

CONNECTIONS

      - Ground equipment according to Division 16 Section "Grounding and Bonding."

      - Connect wiring according to Division 16 Section "Conductors and Cables."

      - Tighten electrical connectors and terminals according to manufacturer's published torque-tightening values.  If manufacturer's torque values are not indicated, use those specified in UL 486A and UL 486B.

FIELD QUALITY CONTROL

      - Perform the following field tests and inspections and prepare test reports:

        - After installing wiring devices and after electrical circuitry has been energized, test for proper polarity, ground continuity, and compliance with requirements.

        - Test GFCI operation with both local and remote fault simulations according to manufacturer's written instructions.

      - Remove malfunctioning units, replace with new units, and retest as specified above.

END OF SECTION   26 27 26