## 14 24 00 - Hydraulic Elevators

### Signal Equipment:

Use non-proprietary and universally maintainable controls and software.  Equipment and software necessary for long-term maintenance shall be available for purchase by any licensed elevator maintenance organization.  (Examples include Car control station and in-car position indicators, Hall push-button stations, Lanterns and gongs, Hall position indicators, etc.)

### Special Features:

Access for persons with disabilities, Fire emergency service, Medical emergency service, Earthquake requirements, and Emergency exit service.

### Closeout Submittals:

Maintenance Tools:  Provide complete list of specialty tools required for general maintenance, including programmable and diagnostic tools.

### Quality Assurance:

Installer Qualifications: Elevator manufacturer installers, or firm with written approval from manufacturer and with five years, minimum of successful experience installing elevators similar to those required for the Project.

### Elevator Maintenance Period:

  - Maintain complete elevator installation for 12 months, minimum beginning at start of warranty period per Procurement and Contracting Requirements.

  - Provide monthly systematic examination, adjustment and lubrication of elevator equipment.  Repair or replace worn electrical and mechanical parts using parts produced by elevator equipment manufacturer. Exception:  Greater frequency required if problems occur with elevator operation.

  - Perform work during non-peak traffic periods.

  - Provide 24-hour emergency call-back service with 2-hour response if the elevator is empty, and 1-hour response time for trapped occupants.

  - Parts:  Locally maintain an adequate stock of parts for replacement and emergency purposes.

  - Maintenance Personnel:  Qualified and approved by elevator manufacturer, and with 5 years, minimum experience.

  - Maintenance Logs:  Prepare logs of each visit and submit to University within 72 hours after visit.

  - Extended Elevator Maintenance Proposal:  Submit proposal to extend maintenance by three years.. Include stipulated sum with premiums due annually.

### Manufacturer/Products:

Elevator:  Capable of producing premium quality commercial hydraulic elevators and accessories to provide a complete installation.

Experience:  Five years, minimum.

Option:  Manufacturer shall either manufacture the major components, or shall maintain a service facility within California with complete service parts for a period of 20 years, minimum after completion of project.

### Fabrication:

  - Doors:  Power operated hollow metal doors with track, rollers and frame; two-point suspension, nonmetallic sheaves; 3-inch diameter, minimum for car doors and 2-1/2-inch diameter for hoistway doors. Finish:  Stainless steel.

  - Hoistway Entrances:  Formed metal with struts, hanger headers, fascia plates, toe guards and Underwriters’ Laboratory labels. Finish:  Match doors.

  - Entrance Protection:  Provide infrared door detectors, complying with ADA and applicable codes.

  - Car Finishes Front Returns:  Stainless steel with inset buttons, swing return panels.

  - Pads:  Provide wall attachment buttons with protective pads.

### Operating Fixtures and Signals:

  - Car Control Station:  Provide service cabinet with built-in, hands-free communications via touch-button for automatic dialing from elevator car, and automatic answering for calling from outside.  Provide door hold-open button.

  - Hall Call Buttons:  Provide illuminated mechanical hall buttons.

  - In-Car Position Indicator:  Provide above elevator hoistway entrance or above control panel for cars serving more than two stops.

  - Lanterns:  Provide wall mounted lanterns at center opening doors, above each hoistway entrance and jamb mounted lanterns at side opening doors with audible signal, one for up-travel, two for down-travel.

### Miscellaneous Items:

  - Battery Operated Emergency Lighting:  Provide in car.

  - Two-Speed Fan:  Provide in car.

  - Other Items:  Provide as required by applicable codes.

### Special Features:

  - Access for Persons with Disabilities:  Comply with CCR Title 24, and ADAAG.

  - Fire Emergency Service:

  - Provide control circuits to comply with CBC.

  - Comply with CCR Title 24.

  - Provide three-position “on-off-bypass” key switch at ground floor.

  - Provide instructions for operation in ground floor cabinet.

  - Connect elevators to smoke detectors in lobbies.

  - Medical Emergency Operation:  Comply with CCR Title 24.

  - Earthquake Requirements:  Comply with applicable codes.

  - Emergency Exit Service:  Provide system to lower elevators to next lower floor level, or to Ground Floor, and doors to open without assistance in power outage.

### Finishes:

Exposed-to-View Surfaces in Car, Machine Room and Hoistway Entrances:

  - Stainless Steel:  Number 4 finish (satin directional polish).

  - Baked Enamel:  Clean, degrease zinc-coated metal surface; one coat zinc oxide primer sprayed and baked; two coats semi-gloss enamel sprayed and baked.

## 14 28 16 - Elevator Controls

Standard: Open protocol, non-proprietary, specified with trouble shooting and operational software, and serviceable by all licensed elevator contractors.

Basis of Design Manufacturer: Motion Control Engineering.  http://www.mceinc.com/.

Elevator Keys: Standard:  Provide 3 keys, installing 1 in elevator pit.

Closeout Submittal: Keys:  Provide manufacturer name and model numbers for keys and coordinate closeout submittal with Section 08 06 05 – Key Schedule.