26 05 29 - SUPPORTING DEVICES

  - PART 1 – GENERAL

    - SECTION INCLUDES

      - Supporting devices for conduit, boxes, and equipment.

  - PART 2 – PRODUCTS

    - ACCEPTABLE MANUFACTURERS

      - Hangers, straps and beam clamps:

        - Efcor.

        - Raco, Inc.

        - Steel City

        - O.Z./Gedney Co.

        - Caddy Fastening System by ERICO Products Inc.

      - Channels and fittings:

        - Kindorf.

        - Unistrut Corp.

      - Anchors:

        - Acherman-Johnson Corp.

        - Phillips Drill Co.

        - Rawl Products Co.

    - mATERIAL AND FABRICATION

      - Hangers, steel cadmium-plated.

      - Straps:  One-hole and two-hole malleable iron, hot-dipped galvanized or steel, cadmium- or zinc-plated.

      - Beam clamps, malleable iron, hot-dipped galvanized or cadmium-plated.

      - Channels and fittings:

        - Channels, hot-dipped galvanized.

        - Fittings, galvanized.

      - Anchors, self-drilling and expansion bolt types.  No wood or fiber plugs or concrete nails are acceptable.

  - PART 3 – EXECUTION

    - INSTALLATION

      - Fasten pad-mounted switchgear, capacitors, switches, and transformers in accord with manufacturer’s recommendation for seismic zone 4. Submit manufacturers details for zone 4 fasteners and attachment or submit details prepared by a California licensed structural engineer.

END OF SECTION 26 05 29