- Section 21 11 00 - Facility Fire-Suppression Water-Service Piping

  - PART 1 GENERAL

    - SECTION INCLUDES

      - Water pipe.

      - Valves.

      - Fire department connections.

      - Private fire hydrants.

      - Bedding and cover materials.

      - Accessories.

    - RELATED REQUIREMENTS

      - Section 03 30 00 - Cast-in-Place Concrete.

      - Section 21 13 00 - Fire-Suppression Sprinkler Systems.

      - Section 31 23 16 - Excavation.

      - Section 31 23 16.13 - Trenching.

      - Section 31 23 23 - Fill.

      - Section 33 05 13 - Manholes and Structures.

      - Section 33 14 16 - Site Water Utility Distribution Piping.

    - REFERENCE STANDARDS

      - ASME B16.3 - Malleable Iron Threaded Fittings: Classes 150 and 300 2016.

      - ASME B16.4 - Gray Iron Threaded Fittings: Classes 125 and 250 2016.

      - ASTM A53/A53M - Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless 2018.

      - ASTM A536 - Standard Specification for Ductile Iron Castings 1984 (Reapproved 2014).

      - ASTM B584 - Standard Specification for Copper Alloy Sand Castings for General Applications 2014.

      - ASTM D3139 - Standard Specification for Joints for Plastic Pressure Pipes using Flexible Elastomeric Seals 1998 (Reapproved 2011).

      - AWWA C110/A21.10 - Ductile-Iron and Gray-Iron Fittings 2012.

      - AWWA C111/A21.11 - Rubber-Gasket Joints for Ductile-Iron Pressure Pipe and Fittings 2017.

      - AWWA C151/A21.51 - Ductile-Iron Pipe, Centrifugally Cast 2017, with Errata (2018).

      - AWWA C502 - Dry-Barrel Fire Hydrants 2018.

      - AWWA C509 - Resilient-Seated Gate Valves for Water Supply Service 2015.

      - AWWA C900 - Polyvinyl Chloride (PVC) Pressure Pipe, 4 In. Through 12 In. (100 mm Through 300 mm), for Water Transmission and Distribution 2016.

    - SUBMITTALS

      - See Section 01 30 00 - Administrative Requirements, for submittal procedures.

      - Product Data:

        - Include data on pipe materials, pipe fittings, valves, and accessories.

        - Provide manufacturer's catalog information.

        - Indicate valve data and ratings.

        - Show grooved joint couplings, fittings, valves, and specialties on drawings and product submittals, specifically identified with the manufacturer's style or series designation.

  - PART 2 PRODUCTS

    - WATER PIPE

      - Ductile Iron Pipe: Listed, AWWA C151/A21.51.

        - Fittings: AWWA C110/A21.10, ductile iron, standard thickness.

        - Joints: AWWA C111/A21.11, styrene butadiene rubber (SBR) or vulcanized SBR rubber gasket with 3/4 inch (19 mm) diameter rods.

      - PVC Pipe: Listed, AWWA C900 Class 100:

        - Fittings: AWWA C111/A21.11, cast iron.

        - Joints: ASTM D3139 compression gasket ring.

    - VALVES

      - Valves: Manufacturer's name and pressure rating marked on valve body.

      - Water Pressure Reducing Valves:

        - 1-1/2 NPS (40 DN) up to and including 8 NPS (200 DN):

          - Function: Reduce higher inlet pressure to an adjustable, constant lower outlet pressure independent of flow rate fluctuations.

          - Pilot-Operated Type: External pilot control.

      - Double Check Detector Valve Assembly, Flanged End:

        - 2-1/2 NPS (65 DN) up to and including 10 NPS (250 DN):

          - Construction:

            - Listed .

            - Body: 300 Series stainless steel, ASTM A536 Grade 65-45-12 ductile iron or [________].

            - Two independently operating, spring-loaded, check valves.

            - Two OSY resilient seated gate valves.

            - Bypass Assembly:

              - Bypass Line: Hydraulically sized to accurately measure low flow.

              - Double check including shut-off valves, and required cocks.

              - Meter with [_____] gallon ([_____] cu ft) readout.

            - Cam-Check:

              - Internally loaded providing positive, drip-tight closure against reverse flow.

              - Stainless steel cam arm and spring, rubber faced disc, and replaceable, thermoplastic seat.

            - Valve Cover:

              - Provides access to all internal parts.

              - Held in place through the use of a single grooved style two-bolt coupling.

    - Fire Department Connections:

      - Free-Standing Inlet:

        - Construction:

          - Listed .

          - Type: Free standing type, ASTM B584 poured brass alloy.

          - Inlets: Two way, 2-1/2 inch (65 DN) female inlets, thread size compatible with fire department hardware.

          - Rated Working Pressure: 175 psi (1200 kPa).

          - Double clapper-valves, rocker-lug caps and chain, and cast-in function-identifying lettering.

          - Finish: Polished brass.

          - Label: Sprinkler - Fire Department Connection.

    - PRIVATE FIRE HYDRANTS

      - Dry-Barrel:

        - Construction:

          - Listed, AWWA C502 and [_______].

          - Rated Working Pressure: 250 psi (1725 kPa).

          - Compression type, opening against system pressure and closing with system pressure.

          - Traffic breakaway type.

        - Hydrant Cap and Stuffing Box: One piece design with water-tight cavity, sealed from contact with water.

        - Operating Nut: One-Piece, bronze construction with protective weather seal, shield or [_____].

        - Nozzles: Tamper resistant, 1/4 turn type with O-ring seals including retaining/locking screws, other suitable nozzle lock or [__________] to prevent inadvertent removal.

        - Main Valve: Provide reinforced, synthetic rubber, completely encapsulated with EPDM or [_____________________].

        - Seat: Provide O-rings to seal drain-way and barrel from water leakage into shoe.

        - Drains to momentarily flush outward when opened to remove debris and complete draining upon closing of the main valve.

    - ACCESSORIES

      - Concrete for Thrust Restraints: Concrete type specified in Section 03 30 00.

      - Tracer Wire:

        - Provide magnetic, detectable conductor with clear plastic covering and imprinted with "Water Service" in large letters.

        - Conductor to be of sufficient length to be continuous over each separate run of nonmetallic pipe.

  - END OF SECTION  21 11 00