## 22 06 00 - Schedule for Plumbing

### Boiler / Chiller Room Plumbing

Provide floor drains / sinks for relief valve drains and to allow for drain down of closed loop systems. Coordinate locations with equipment layout so that piped equipment drains will not be a trip hazard in service aisles. Select floor drains/sinks to contain spill over and splashing due to equipment drain discharge.

Provide make up water through a RP backflow preventer for each closed loop system.

### Plaster / Sand Use.

Rooms where plaster or other sediment material is used shall be equipped with a dedicated above grade sand trap on the drain outlet of each sink. Typical applications include art studios using plaster, anthropology labs using plaster for bone castings, etc.

### Dark Rooms

Provide RP back flow preventers for hot and cold water to dark room sinks.

### Fume Hoods

For each plumbing fume hood plumbing service, provide a manual isolation valve and union at the piping drop above each fume hood so that the hood can be easily removed with minimal disruption of building piping.

### Commercial Kitchens

Per City of San Luis Obispo Waste Water Discharge Ordinance, a large outdoor grease trap is typically required. Position grease trap to allow for easy access for pumping and minimal nuisance odors at occupied locations while pumping.