## 22 42 13 - Commercial Water Closets, Urinals, and Bidets

### Toilets

- Student Apartments:

  - Toilet shall be 1.28 GPF vitreous china round front bowl, with direct flow priming jet and reverse trap. Hydraulic performance exceeding ANSI A112.19.2 requirements.

  - Seat: All plastic, closed front with cover, stainless steel hinge.

  - Campus Preference:

    - 1.28 HET Floor Mount Floor Discharge – American Standard 2234.001.020 1.1 - 1.6

    - 1.28 HET Floor Mount Floor Discharge (ADA) – American Standard 3461.001.020 1.1 - 1.6

- Public Restrooms (including dormitories):

  - Toilets shall be 1.28 GPF, wall hung with support carrier, vitreous china, elongated, flush valve type exceeding ANSI A112.19.2 requirements.

  - Campus Preference:

    - American Standard 2257.101.020 with Afwall 1.1 – 1.6 (1.28)

    - 1.28 GPF HET manual Toilet (No Piston Valve) – Zurn Z6000 AV Model

    - 1.28 GPF HET Sensor Toilet (No Piston) – ZER6000 CPM Medel

  - Flush valve: 1.28 GPF

  - Flush Valves - Toilets (with infrared sensors):

    - Zurn ZER6000AV-ONE-CPM high efficiency flushometer valve

    - Campus no longer installs Flush Valves - Toilets without infrared sensors.

  - Seat: All plastic, open front elongated without cover; stainless steel hinge.

- Alternate toilet for single stall public rest rooms where light use is expected: Toilet shall be 1.28 GPF with hydro-pneumatic pressure assisted flush, vitreous china, floor mounted, elongated bowl, exceeding ANSI A112.19.2 requirements. Seat: All plastic, open front elongated without cover; stainless steel hinge.

  - Toilet carrier manufactures Zurn, Josam, Mifab and J.R. Smith

  - Not Recommended:

    - Toilet:  Zurn Z5615 Series, Zurn Z5655 Series, and Zurn Z5665 Series 1.28 GPF Elongated vitreous china toilet.  The toilet bowls are too shallow for proper water scouring when flushed.

    - Toilet Seat: Enlongated Open Front Seat – Bemis 1955SSCT

### Urinals

Campus Standard, as appropriate for use/scope:

- Washbrook 0.125 GPF FloWise Washout Top Spud Urinal, or

- Z5758 “The Retrofit Pint” 0.125 gpf Ultra Low Consumption Urinal System (21” – 24” Footprint)

- Zurn-ZER 6003AV-CPM Model Sensor Operated Battery Powered Flush Valve for ¾” Urinals

### Trap Adapters:

Standard:  Use when waste line has a tubular trap.  Purpose is to allow for easier maintenance.

Preferred Manufacturer and Model:  Arrowhead Brass Products, #6001A, 1-1/2” M.I.P. x 1-1/2” Tube Size – Brass Nut, Brass Ferrule with stop.  Male in Female UPC-1003.2. http://www.arrowheadbrass.com/products/

Flushometers:

Flush Valves: Standard: Zurn