- Section 22 47 00 – drinking fountains and water coolers

  - PART 1 GENERAL

SECTION INCLUDES

      - Electric water coolers.

      - Drinking fountains/Hydration Stations.

RELATED REQUIREMENTS

      - Section 22 05 00 – Common Work Results for Plumbing

      - Section 22 10 05 – Plumbing Piping.

      - Section 22 11 16 – Domestic Water Piping

      - Section 22 13 00 – Facility Sanitary Sewerage

      - Section 22 30 00 – Plumbing Equipment.

      - Section 22 40 00 – Plumbing Fixtures

SUBMITTALS

      - Product Data: Provide catalog illustrations of fixtures, sizes, rough-in dimensions, utility sizes, trim, and finishes.

  - PART 2 PRODUCTS

GENERAL REQUIREMENTS

      - Potable Water Systems: Provide plumbing fittings and faucets that comply with NSF 61 and NSF 372 for maximum lead content; label pipe and fittings.

DRINKING FOUNTAINS and water coolers

      - Water Cooler: Electric, mechanically refrigerated; surface mounted, ADA compliant; stainless steel top, vinyl on steel body, elevated anti-squirt bubbler with stream guard, automatic stream regulator, push button, mounting bracket; integral air-cooled condenser and stainless-steel grille.

        - Capacity: 8 gallons per hour (30.3 liters per hour) of 50 degrees F (10 degrees C) water with inlet at 80 degrees F (27 degrees C) and room temperature of 90 degrees F (32 degrees C), when tested in accordance with ASHRAE Std 18.

        - Electrical: 115 V, 60 Hertz compressor, 6 foot (2 m) cord and plug for connection to electric wiring system including grounding connector.

      - Hydration Station:

        - Elkay Model LZWSSM Surface Mount bottle filling station. Sanitary, touchless activation with auto 20-second shut-off.

          - WaterSentry Plus 3000-gallon capacity filtration system, certified to NSF/ANSI 42 & 53 (Lead, Class 1 Particulate, Chlorine, Taste 7 Odor)

          - Integrated silver ion anti-microbial protection

          - Fill rate: 1.5 gpm; 1.1 gpm when connected to a remote chiller

          - Laminar flow to reduce splash

          - Real drain system

          - Visual user interface display includes:

          - Green Ticker counts bottles saved from waste

          - LED visual filter monitor indicates when to replace filter

          - Optional remote chiller can be installed within 15 feet of unit to deliver chilled drinking water.

EMERGENCY EYE AND FACE WASH

      - Emergency Wash: ANSI Z358.1; wall-mounted, self-cleaning, non-clogging eye and face wash with quick opening, full-flow valves, stainless steel eye and face wash receptor, twin eye wash heads and face spray ring, stainless steel dust cover, copper alloy control valve and fittings.

PART 3 EXECUTION

INSTALLATION

      - Install components level and plumb.

  - END OF SECTION  22 47 00