## 23 09 13 - Instrumentation and Control Devices for HVAC

### Temperature Sensors /

Resistance Temperature Detectors (RTD’s):

- Standard:  Siemens 1000 Ohm Platinum RTD, Model Number PTM6.2P1K.

- Exception:  Thermistors are required in some zone applications such as VAV boxes, and may only be used in those areas.

- Function:  Use for air handlers, Hot Water (HW) and Chilled Water (CHW).  Do not install in piping tee.  Connect to Energy Management System (EMS) by Siemens.

### Differential Pressure Sensors:

Resistance Temperature Detectors (RTD’s):

- Siemens Sitrans 7MF4433 with 3-valve manifold and local display.

- Standard:  Emerson Process Management, Rosemount Model #1151 Pressure Transmitter.    Connect to Energy Management System (EMS) by Siemens.  Specify pressure range for 150% of maximum expected differential pressure.

- Function:  Measure differential pressure for monitoring and control of variable speed pumps.

- Website:  http://www.emersonprocess.com/rosemount/Products/Pressure/m1151.html

### Motor Controls:

Variable Frequency Drives (VFD’s):

- Campus Standard:  ABB ACH550.  Enclosure: UL (NEMA) Type 12.  Integral disconnect.  No bypass.  No known equal.

- Function:  Connect to Campus Energy Management System (EMS) by Siemens as a Field Level Network (FLN) device to provide direct communication (not hardwired start/stop/status).  Proof through drive and via current switches.