- Section 23 21 23 - Hydronic Pumps

  - PART 1 GENERAL

    - REFERENCE STANDARDS

      - NEMA OS 1 - Sheet-Steel Outlet Boxes, Device Boxes, Covers, and Box Supports 2013.

      - NFPA 70 - National Electrical Code Most Recent Edition Adopted by Authority Having Jurisdiction, Including All Applicable Amendments and Supplements.

      - UL 778 - Standard for Motor-Operated Water Pumps Current Edition, Including All Revisions.

    - SUBMITTALS

      - See Section 01 30 00 - Administrative Requirements, for submittal procedures.

      - Product Data: Provide certified pump curves showing performance characteristics with pump and system operating point plotted. Include NPSH curve when applicable. Include electrical characteristics and connection requirements.

  - PART 2 PRODUCTS

    - HVAC PUMPS - GENERAL

      - Provide pumps that operate at specified system fluid temperatures without vapor binding and cavitation, are non-overloading in parallel or individual operation, and operate within 25 percent of midpoint of published maximum efficiency curve.

      - Products Requiring Electrical Connection: Listed and classified by UL or testing agency acceptable to Authority Having Jurisdiction as suitable for the purpose specified and indicated.

    - SYSTEM LUBRICATED CIRCULATORS

      - Type: Horizontal shaft, single stage, direct connected with multiple speed wet rotor motor for in-line mounting, for 140 psi (965 kPa) maximum working pressure, 230 degrees F (110 degrees C) maximum water temperature.

      - Casing: Cast iron with flanged pump connections.

      - Impeller, Shaft, Rotor: Stainless Steel.

      - Bearings: Metal Impregnated carbon (graphite) and ceramic.

      - Motor: Impedance protected, multiple speed, with external speed selector.

    - IN-LINE CIRCULATORS

      - Type: Horizontal shaft, single stage, direct connected, with resiliently mounted motor for in-line mounting, oil lubricated, for 175 psi (1200 kPa) maximum working pressure.

      - Casing: Cast iron, with flanged pump connections.

      - Impeller: Non-ferrous keyed to shaft.

      - Bearings: Oil-lubricated bronze sleeve.

      - Shaft: Alloy steel with bronze sleeve, integral thrust collar.

      - Seal: Mechanical seal, 225 degrees F (107 degrees C) maximum continuous operating temperature.

      - Drive: Flexible coupling.

      - Electrical Characteristics:

        - Wiring Terminations: Provide terminal lugs to match branch circuit conductor quantities, sizes, and materials indicated. Enclose terminal lugs in terminal box sized to NFPA 70.

    - VERTICAL IN-LINE PUMPS

      - Type: Vertical, single stage, close coupled, radially or horizontally split casing, for in-line mounting, for 175 psi (1200 kPa) working pressure.

      - Casing: Cast iron, with suction and discharge gauge port, casing wear ring, seal flush connection, drain plug, flanged suction and discharge.

      - Impeller: Bronze, fully enclosed, keyed directly to motor shaft or extension.

      - Shaft: Carbon steel with stainless steel impeller cap screw or nut and bronze sleeve.

      - Seal: Mechanical seal, 225 degrees F (107 degrees C) maximum continuous operating temperature.

      - Electrical Characteristics:

        - Wiring Terminations: Provide terminal lugs to match branch circuit conductor quantities, sizes, and materials indicated. Enclose terminal lugs in terminal box sized to NFPA 70.

    - CLOSE COUPLED PUMPS

      - Type: Horizontal shaft, single stage, close coupled, radially split casing, for 125 psi (860 kPa) maximum working pressure.

      - Casing: Cast iron, with suction and discharge gauge ports, renewable bronze casing wearing rings, seal flush connection, drain plug, flanged suction and discharge.

      - Impeller: Bronze, fully enclosed, keyed to motor shaft extension.

      - Shaft: Stainless steel.

      - Seal: Mechanical seal, 225 degrees F (107 degrees C) maximum continuous operating temperature.

      - Electrical Characteristics:

        - Wiring Terminations: Provide terminal lugs to match branch circuit conductor quantities, sizes, and materials indicated. Enclose terminal lugs in terminal box sized to NFPA 70.

    - BASE-MOUNTED PUMPS

      - Type: Horizontal shaft, single stage, direct connected, radially or horizontally split casing, for 125 psi (860 kPa) maximum working pressure.

      - Casing: Cast iron, or ductile iron with suction and discharge gauge ports, renewable bronze casing wearing rings, seal flush connection, drain plug, flanged suction and discharge.

      - Impeller: Bronze, fully enclosed, keyed to shaft.

      - Bearings: Oil lubricated roller or ball bearings.

      - Shaft: Alloy steel with copper, bronze, or stainless steel shaft sleeve.

      - Seal: Mechanical seal, 225 degrees F (107 degrees C) maximum continuous operating temperature.

      - Drive: Flexible coupling with coupling guard.

      - Baseplate: Cast iron or fabricated steel with integral drain rim.

      - Electrical Characteristics:

        - Wiring Terminations: Provide terminal lugs to match branch circuit conductor quantities, sizes, and materials indicated. Enclose terminal lugs in terminal box sized to NFPA 70.

    - DUAL DRIVE PUMPING SYSTEM

      - Pumping System: Horizontal split case, base-mounted pump with two motors, operating at 1750 rpm and 1150 rpm, assembled on integral base with control cabinet.

      - Control Cabinet: NEMA OS 1, UL approved enclosure with individual circuit breakers, magnetic starters with overload protection, running lights, separate 115V fused control circuit, hands-off-automatic switches, motor failure alarm with manual reset, pre-wired.

      - Electrical Characteristics:

        - Wiring Terminations: Provide terminal lugs to match branch circuit conductor quantities, sizes, and materials indicated. Enclose terminal lugs in terminal box sized to NFPA 70.

  - PART 3 EXECUTION

    - INSTALLATION

      - Install in accordance with manufacturer's instructions.

      - Provide access space around pumps for service. Provide no less than minimum space recommended by manufacturer.

      - Decrease from line size with long radius reducing elbows or reducers. Support piping adjacent to pump such that no weight is carried on pump casings. For close-coupled or base-mounted pumps, provide supports under elbows on pump suction and discharge line sizes 4 inches (102 mm) and over.

      - Check, align, and certify alignment of base-mounted pumps prior to start-up.

  - END OF SECTION  23 21 23