SECTION 26 05 19 - CONDUCTORS

  - PART 1 – GENERAL

    - SECTION INCLUDES

      - Conductors for power, lighting, sound, communication and control, including:

        - Conductors for general wiring.

        - Multi-conductor cable.

        - Flexible cords and cables.

    - RELATED WORK SPECIFIED ELSEWHERE

      - Conductor identification:  Section 26 05 53.

      - Conductor connections and devices:  Section 26 05 21.

      - Wiring Devices: Section 26 27 26.

      - Grounding: Section 26 05 26.

    - REFERENCE SPECIFICATIONS AND STANDARDS

      - National Electrical Code.  Reference Articles 250, 310, and 800.

  - PART 2 – PRODUCTS

    - ACCEPTABLE MANUFACTURERS

      - Cable products as manufactured by the following manufacturers only are acceptable in meeting specified requirements:

        - General Cable Co.

        - Rome Cable.

        - American Insulated Wire.

        - BICC Cable Corp.

        - 5. Belden Inc.

    - MATERIAL AND FABRICATION

      - Conductors for general wiring:  Thermoplastic insulation rated for 600V manufactured in accord with UL 83.

        - Copper conductors, 3/4 hard drawn.  Type THHN/THWN or XHHN/XHHW where required by location.  Markings on cables shall be clearly marked with size and type.  Markings shall be white lettering with black jacketing for conductor sizes of #6 AWG or larger.  Indentations for lettering are not acceptable.  Cable sizes #8 AWG and larger shall be stranded conductors.

  - PART 3 – EXECUTION

    - USE

      - Conductors for general wiring:

        - Minimum 90°C temperature rated insulation on conductors, except minimum 105°C temperature rated insulation on conductors in conduits exposed on roof.

        - Stranded conductors at motors and other applications where subject to vibration.

        - Minimum size conductors for power and lighting: #12 AWG, with THHN/THWN insulation except where noted.

        - Minimum size conductors for motor control circuits: #14 AWG stranded with THHN/THWN insulation except where noted.

        - All cable conductors of 3-phase circuits or single-phase shall be of the same type, mixing stranded conductors for some phases with others as solid is not acceptable.

        - Multi-conductor cable: Only for use in low voltage control circuits.

      - Ground conductors:

        - Bare copper conductor may be used for equipment ground only.

          - Install ground conductors in all feeder conduits and all non-metallic conduits as required by Electrical Code and Section 26 05 26.

        - Insulated ground conductors:

          - Ground conductor insulation color:  Green.

          - Isolated ground conductor insulation color:  Green with white stripe.

    - INSPECTION

      - Check conduit system for damage and loose connections, replace damaged sections.

      - Check for caps at conduit openings.  Make sure that inside of conduit is free of dirt and moisture.

      - Pull mandrel, one size smaller than the conduit, through entire length of all underground conduits prior to conductor installation.

    - INSTALLATION

      - Conductors for general wiring:

        - Color code conductors insulation as follows:

| SYSTEM VOLTAGE |  |  |
| --- | --- | --- |
| Conductor | 208Y/120 | 480Y/277 |
| Phase A | Black | Brown |
| Phase B | Red | Orange |
| Phase C | Blue | Yellow |

- For conductors #6 AWG or larger, permanent plastic colored tape may be used to mark conductor end in lieu of coded insulation.  Tape shall cover not less than 2 in. of conductor insulation within enclosure.

- When pulling conductors do not exceed manufacturer's recommended values.

- Use polypropylene or nylon ropes for pulling conductors.

- Prior to energizing, ensure that cables are:

        - Free from short circuits and grounds.

        - Free from mechanical and electrical defects.

- Test all conductors in accordance with Section 26 05 53.

- Conductor identification:

- Feeders:  Identify with corresponding circuit designation at over-current device and load ends, at all splices, and in pull boxes.

- Provide labels as indicated in Section 26 05 53, and on plans and details.

- Multi-conductor and twin axial cables:  Install cables end-to-end without splices.

END OF SECTION 26 05 19