- Section 33 14 16 - Site Water Utility Distribution Piping

  - PART 1 GENERAL

    - SECTION INCLUDES

      - Water pipe for site conveyance lines.

      - Pipe valves.

      - Fire hydrants.

    - RELATED REQUIREMENTS

      - Section 03 30 00 - Cast-in-Place Concrete: Concrete for thrust restraints.

      - Section 21 11 00 - Facility Fire-Suppression Water-Service Piping.

      - Section 31 23 16.13 - Trenching: Excavating, bedding, and backfilling.

      - Section 33 05 13 - Manholes and Structures.

    - REFERENCE STANDARDS

      - ASME B16.3 - Malleable Iron Threaded Fittings: Classes 150 and 300 2016.

      - ASME B16.4 - Gray Iron Threaded Fittings: Classes 125 and 250 2016.

      - ASME B16.18 - Cast Copper Alloy Solder Joint Pressure Fittings 2018.

      - ASME B16.22 - Wrought Copper and Copper Alloy Solder-Joint Pressure Fittings 2018.

      - ASTM A53/A53M - Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless 2018.

      - ASTM B88 - Standard Specification for Seamless Copper Water Tube 2016.

      - ASTM D2466 - Standard Specification for Poly(Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 40 2017.

      - ASTM D2467 - Standard Specification for Poly(Vinyl Chloride) (PVC) Plastic Pipe Fittings, Schedule 80 2015.

      - ASTM D3139 - Standard Specification for Joints for Plastic Pressure Pipes using Flexible Elastomeric Seals 1998 (Reapproved 2011).

      - AWS A5.8M/A5.8 - Specification for Filler Metals for Brazing and Braze Welding 2011 (Amended 2012).

      - AWWA C111/A21.11 - Rubber-Gasket Joints for Ductile-Iron Pressure Pipe and Fittings 2017.

      - AWWA C509 - Resilient-Seated Gate Valves for Water Supply Service 2015.

      - AWWA C600 - Installation of Ductile-Iron Water Mains and Their Appurtenances 2017.

      - AWWA C900 - Polyvinyl Chloride (PVC) Pressure Pipe, 4 In. Through 12 In. (100 mm Through 300 mm), for Water Transmission and Distribution 2016.

    - SUBMITTALS

      - See Section 01 30 00 - Administrative Requirements, for submittal procedures.

      - Product Data: Provide data on pipe materials, pipe fittings, valves and accessories.

      - Project Record Documents: Record actual locations of piping mains, valves, connections, thrust restraints, and invert elevations. Identify and describe unexpected variations to subsoil conditions or discovery of uncharted utilities.

  - PART 2 PRODUCTS

    - WATER PIPE

      - Ductile Iron Pipe: AWWA C151/A21.51:

        - Fittings: Ductile iron, standard thickness.

        - Joints: AWWA C111/A21.11, Styrene butadiene rubber (SBR) or vulcanized SBR gasket with rods.

      - Copper Tubing: ASTM B88, Type K, Annealed:

        - Fittings: ASME B16.18, cast copper, or ASME B16.22, wrought copper.

        - Joints: Compression connection or AWS A5.8M/A5.8, BCuP silver braze.

      - PVC Pipe: AWWA C900 Class 100:

        - Fittings: AWWA C111/A21.11, Schedule 40 per ASTM D2466 or schedule 80 per ASTM D2467.

        - Joints: ASTM D3139 compression gasket ring.

      - Trace Wire: Magnetic detectable conductor, clear plastic covering, imprinted with "Water Service" in large letters.

    - VALVES

      - Valves: Manufacturer's name and pressure rating marked on valve body.

      - Gate Valves Up To 3 Inches (75 mm):

        - Brass or Bronze body, non-rising stem, inside screw, single wedge or disc, compression ends, with control rod, post indicator, valve key, and extension box.

      - Gate Valves 3 Inches (75 mm) and Over:

        - AWWA C509, iron body, bronze trim, non-rising stem with square nut, single wedge, resilient seat, flanged ends, control rod, post indicator, valve key, and extension box.

      - Ball Valves Up To 2 Inches (50 mm):

        - Brass body, Teflon coated brass ball, rubber seats and stem seals, Tee stem pre-drilled for control rod, AWWA inlet end, compression outlet with electrical ground connector, with control rod, valve key, and extension box.

    - ACCESSORIES

      - Concrete for Thrust Restraints: Concrete type specified in Section 03 30 00.

      - Backflow Preventer: [________].

      - Meter: [________].

      - Manhole and Cover: Refer to Section 33 05 13.

  - PART 3 EXECUTION

    - INSTALLATION - PIPE

      - Install ductile iron piping and fittings to AWWA C600.

      - Route pipe in straight line.

      - Install pipe to allow for expansion and contraction without stressing pipe or joints.

      - Slope water pipe and position drains at low points.

    - INSTALLATION - VALVES AND HYDRANTS

      - Set valves on solid bearing.

      - Center and plumb valve box over valve. Set box cover flush with finished grade.

      - Set hydrants plumb; locate pumper nozzle perpendicular to and facing roadway in accordance with Section 21 11 00.

      - Set hydrants to grade, with nozzles at least 20 inches (500 mm) above ground in accordance with Section 21 11 00.

  - END OF SECTION  33 14 16