- Section 21 12 00 - Fire-Suppression Standpipes

  - PART 1 GENERAL

    - RELATED REQUIREMENTS

      - Section 21 05 00 - Common Work Results for Fire Suppression: Fire protection piping.

      - Section 21 05 23 - General-Duty Valves for Water-Based Fire-Suppression Piping.

    - REFERENCE STANDARDS

      - NFPA 14 - Standard for the Installation of Standpipe and Hose Systems 2019.

      - UL 405 - Fire Department Connection Devices Current Edition; Including All Revisions.

  - PART 2 PRODUCTS

    - FIRE DEPARTMENT CONNECTIONS

      - Type: Free standing made of corrosion resistant metal complying with UL 405.

        - Sleeve: Brass, 18 inches (460 mm) height.

  - PART 3 EXECUTION

    - INSTALLATION

      - Install in accordance with manufacturer's instructions.

      - Install in accordance with NFPA 14.

      - Connect standpipe system to water source ahead of domestic water connection.

      - Flush entire system of foreign matter.

      - Buried piping and fittings:

        - Cement-mortar lined, ductile iron pipe conforming to AWWA  C-151, Class 200, 21/45 with Tyton or as approved, mechanical joints and fittings conforming to NFPA-24.

        - Install pipe joints anchored with tie rods and restraints. Provide concrete thrust blocks at elbows and offsets conforming to NFPA-13 and NFPA-24.

        - Other types of UL/FM reviewed piping including PVC C900 Class 200 may be used as approved by University's Representative and the State Fire Marshal.

        - Thrust block installation shall be inspected by State Fire Marshal.

      - Above ground piping and fittings:

        - Standard weight, Schedule 40, welded and seamless black steel, ASTM A-135 or A-53 pipe conforming to NFPA-13.

        - Fittings for pipe sizes 2-1/2 inch and smaller shall be malleable iron, black, 150 lb. standard or cast iron, 175 lb. WP, screwed ends.

        - Fittings for pipe sizes 3 inch and larger may be as above or weld fittings, ANSI 16.9, Schedule 40, flanged or welded fittings, cast iron, 175 lb. WP.

        - Clamp type UL/FM approved fittings may be used on concealed piping where listed by the State Fire Marshal.

        - Piping installed outdoors shall be galvanized.

      - Alternate piping system to be Victaulic, Grinnel, or equal grooved piping systems.

      - CPVC piping may be used in locations approved by NFPA 13 and the State Fire Marshal.

END OF SECTION  21 12 00