26 05 21-CONDUCTOR CONNECTIONS AND DEVICES

  - PART 1 – GENERAL

    - SECTION INCLUDES

      - Conductor connections and devices.

  - PART 2 – PRODUCTS

    - ACCEPTABLE MANUFACTURERS

      - Conductor connectors for general wiring:

        - Size Nos. 6 or larger, copper:

          - Ilsco Corp.

          - Thomas & Betts Co.

          - Burndy Corp.

          - Square D Versa-Crimp.

        - Size Nos. 1/0 or larger, aluminum:

          - Thomas Betts Co.

          - Square D Versa-Crimp.

      - Insulating tape:

        - Minnesota Mining & Mfg. Co. (3M).

        - Plymouth Rubber Co.

    - MATERIAL AND FABRICATION

      - Conductor connectors for general wiring:

        - Splice and terminate with compression or pressure type connectors and terminal lugs.

        - Outdoor or wet locations:  Silicon filled safety connectors by King Technology, Inc. or Owner-approved equivalent.

      - Multi-conductor cables:

        - Ring tongue terminal lug with insulated grip and insulation support:

      - Connector sealing packs for splices that require complete protection from dampness and water.

        - Scotchlok Nos. 3576, 3577 and 3578, by 3M Company.

      - Electrical insulating resin:  Scotchcast Electrical Insulating Resin 400 by 3M Company.

  - PART 3 – EXECUTION

    - INSTALLATION

      - Terminate and splice feeder conductors as follows:

        - Strip insulation by penciling or paring very carefully so as not to damage the conductor.

        - Remove enough insulation so that conductor can be fully inserted into connector sleeve or terminal lug.

        - Apply oxide inhibitor recommended by connector manufacturer to all exposed conductors and wire brush to fully penetrate spaces between strands.

        - Use hydraulic type compression tool:  Thomas & Betts Type TBM15 or Square D Versa-Crimp.

        - Operate pump until bypass has been reached.

        - Place full amount of crimps on connectors and terminal lugs as recommended by manufacturer.

        - Use compression type connector and terminal lugs for splices and terminations.

        - Apply torque values specified by terminal lug manufacturer.

        - Use "breakaway" type torque wrench to prevent over tightening.

      - Insulate splices with plastic electrical tape:  Scotch No. 33+ or Tomic No. 1T.

      - Terminate all control wires with terminal lugs on barriered terminal boards.  If splices are needed, use same procedure, installing terminal board in a junction box for protection.

      - Provide lugs for conductors terminating on secondary side of substation.

END OF SECTION 26 05 21